## 85-95
|  | Supply Fan |  | Heat Pump Cooling | [8 empty] | Heat Pump Heating | [7 empty] | Unit Electrical
Tag | Model | CFM | ESP | Net Total Capacity | Net Sensible Capacity | EAT DB/WB | LAT DB/WB | Fluid Flow | EWT | LWT | WPD | EER* | Total Capacity | EAT DB | LAT DB | EWT | LWT | Fluid Flow | WPD | COP* | Unit Amps | Unit MCA | Unit MFS | Unit Voltage
HP-1.0T | 50PSV012 | 400 | 0.450 | 11.5 | 8.4 | 76/65 | 56.1/55.1 | 2.7 | 85.0 | 95.0 | 2.8 | 14.9 | 15.7 | 70.0 | 107 | 70.0 | 60.6 | 2.7 | 9.5 | 5.1 | 5.56 | 7 | 15 | 208/230-1-60
HP-1.5T | 50PSV018 | 650 | 0.540 | 18.2 | 13.4 | 76/65 | 55.2/54.7 | 4.3 | 85.0 | 95 | 7.8 | 16.4 | 22.2 | 70.0 | 104.5 | 70.0 | 61.4 | 4.3 | 7.8 | 5.3 | 10.2 | 12 | 15 | 208/230-1-60
HP-2.0T | 50PSV024 | 800 | 0.500 | 24.5 | 18 | 76/65 | 55.1/54.6 | 5.7 | 85.0 | 95 | 6.2 | 18.2 | 31 | 70.0 | 105.9 | 70.0 | 60.9 | 5.7 | 6.2 | 5.7 | 16.3 | 20 | 30 | 208/230-1-60
HP-2.5T | 50PSV030 | 950 | 0.300 | 26.5 | 20.2 | 76/65 | 56.3/55.6 | 6.1 | 85.0 | 95.1 | 2.5 | 16.6 | 32.7 | 70.0 | 101.9 | 70.0 | 61.1 | 6.1 | 2.5 | 5.9 | 16.9 | 20 | 30 | 208/230-1-60
HP-3.0T | 50PSV036 | 1,200 | 0.483 | 33.7 | 25.7 | 76/65 | 56.2/55.6 | 7.8 | 85.0 | 95 | 3.6 | 17.2 | 45 | 70.0 | 104.7 | 70.0 | 60.2 | 7.8 | 3.6 | 5.6 | 22.8 | 27 | 40 | 208/230-1-60
HP-3.5T | 50PSV042 | 1,400 | 0.500 | 40 | 32.1 | 76/65 | 57.1/56.6 | 9.1 | 85.0 | 95.1 | 4.7 | 18.2 | 47 | 70.0 | 97.7 | 70.0 | 61.2 | 9.1 | 4.7 | 6 | 21.4 | 25 | 40 | 208/230-1-60
HP-4.0T | 50PSV048 | 1,600 | 0.600 | 46 | 36.4 | 76/65 | 56.8/56.3 | 10.6 | 85.0 | 95.1 | 6.2 | 17.2 | 57.1 | 70.0 | 100 | 70.0 | 60.9 | 10.6 | 6.2 | 5.3 | 25.9 | 31 | 50 | 208/230-1-60
HP-5.0T | 50PSV060 | 2,000 | 0.525 | 56.5 | 42.3 | 76/65 | 56.4/55.5 | 13.3 | 85.0 | 95 | 9.3 | 16.2 | 79.2 | 70.0 | 106.6 | 70.0 | 59.9 | 13.3 | 9.3 | 5.7 | 32.6 | 39 | 60 | 208/230-1-60
HP-6.0T | 50PSV070 | 2,300 | 0.675 | 62.6 | 48.6 | 75/65 | 56.5/55.9 | 14.7 | 85.0 | 95 | 5.7 | 16.2 | 90.2 | 70.0 | 106.3 | 70.0 | 59.6 | 14.7 | 5.7 | 5.6 | 33.9 | 40 | 60 | 208/230-1-60
* EER - COP AT AHRI
- For 1/3 Ton or 3/4 Ton units, please contact your sales representative
- Units are also available in horizontal configuration

## 87-97
|  | Supply Fan |  | Heat Pump Cooling | [8 empty] | Heat Pump Heating | [7 empty] | Unit Electrical
Tag | Model | CFM | ESP | Net Total Capacity | Net Sensible Capacity | EAT DB/WB | LAT DB/WB | Fluid Flow | EWT | LWT | WPD | EER* | Total Capacity | EAT DB | LAT DB | EWT | LWT | Fluid Flow | WPD | COP* | Unit Amps | Unit MCA | Unit MFS | Unit Voltage
HP-1.0T | 50PSV012 | 400 | 0.450 | 11.4 | 8.4 | 76/65 | 56.3/55.2 | 2.7 | 87 | 97 | 2.8 | 14.9 | 15.7 | 70.0 | 107 | 70.0 | 60.6 | 2.7 | 9.5 | 5.1 | 5.56 | 7 | 15 | 208/230-1-60
HP-1.5T | 50PSV018 | 650 | 0.540 | 18 | 13.3 | 76/65 | 55.4/54.8 | 4.3 | 87 | 97 | 7.8 | 16.4 | 22.2 | 70.0 | 104.5 | 70.0 | 61.4 | 4.3 | 7.8 | 5.3 | 10.2 | 12 | 15 | 208/230-1-60
HP-2.0T | 50PSV024 | 800 | 0.500 | 24.3 | 17.9 | 76/65 | 55.2/54.7 | 5.7 | 87 | 97 | 6.2 | 18.2 | 31 | 70.0 | 105.9 | 70.0 | 60.9 | 5.7 | 6.2 | 5.7 | 16.3 | 20 | 30 | 208/230-1-60
HP-2.5T | 50PSV030 | 950 | 0.300 | 26.2 | 20.1 | 76/65 | 56.4/55.8 | 6.1 | 87 | 97 | 2.5 | 16.6 | 32.7 | 70.0 | 101.9 | 70.0 | 61.1 | 6.1 | 2.5 | 5.9 | 16.9 | 20 | 30 | 208/230-1-60
HP-3.0T | 50PSV036 | 1,200 | 0.483 | 33.3 | 25.6 | 76/65 | 56.3/55.7 | 7.8 | 87 | 97 | 3.6 | 17.2 | 45 | 70.0 | 104.7 | 70.0 | 60.2 | 7.8 | 3.6 | 5.6 | 22.8 | 27 | 40 | 208/230-1-60
HP-3.5T | 50PSV042 | 1,400 | 0.500 | 39.5 | 31.9 | 76/65 | 57.2/56.7 | 9.1 | 87 | 97 | 4.7 | 18.2 | 47 | 70.0 | 97.7 | 70.0 | 61.2 | 9.1 | 4.7 | 6 | 21.4 | 25 | 40 | 208/230-1-60
HP-4.0T | 50PSV048 | 1,600 | 0.600 | 45.5 | 36.4 | 76/65 | 57.0/56.4 | 10.6 | 87 | 97 | 6.2 | 17.2 | 57.1 | 70.0 | 100 | 70.0 | 60.9 | 10.6 | 6.2 | 5.3 | 25.9 | 31 | 50 | 208/230-1-60
HP-5.0T | 50PSV060 | 2,000 | 0.525 | 55.5 | 41.8 | 76/65 | 56.7/55.7 | 13.3 | 87 | 97 | 9.3 | 16.2 | 79.2 | 70.0 | 106.6 | 70.0 | 59.9 | 13.3 | 9.3 | 5.7 | 32.6 | 39 | 60 | 208/230-1-60
HP-6.0T | 50PSV070 | 2,300 | 0.675 | 61.9 | 48.2 | 75/65 | 56.6/56.0 | 14.7 | 87 | 97 | 5.7 | 16.2 | 90.2 | 70.0 | 106.3 | 70.0 | 59.6 | 14.7 | 5.7 | 5.6 | 33.9 | 40 | 60 | 208/230-1-60
* EER - COP AT AHRI
- For 1/3 Ton or 3/4 Ton units, please contact your sales representative
- Units are also available in horizontal configuration

## 85-97
|  | Supply Fan |  | Heat Pump Cooling | [8 empty] | Heat Pump Heating | [7 empty] | Unit Electrical
Tag | Model | CFM | ESP | Net Total Capacity | Net Sensible Capacity | EAT DB/WB | LAT DB/WB | Fluid Flow | EWT | LWT | WPD | EER* | Total Capacity | EAT DB | LAT DB | EWT | LWT | Fluid Flow | WPD | COP* | Unit Amps | Unit MCA | Unit MFS | Unit Voltage
HP-1.0T | 50PSV012 | 400 | 0.450 | 11.4 | 8.4 | 76/65 | 56.3/55.2 | 2.7 | 85 | 97 | 2.8 | 14.9 | 15.7 | 70.0 | 107 | 70.0 | 60.6 | 2.7 | 9.5 | 5.1 | 5.56 | 7 | 15 | 208/230-1-60
HP-1.5T | 50PSV018 | 650 | 0.540 | 18.2 | 13.4 | 76/65 | 55.2/54.7 | 4.3 | 85 | 97 | 7.8 | 16.4 | 22.2 | 70.0 | 104.5 | 70.0 | 61.4 | 4.3 | 7.8 | 5.3 | 10.2 | 12 | 15 | 208/230-1-60
HP-2.0T | 50PSV024 | 800 | 0.500 | 24.2 | 17.9 | 76/65 | 55.3/54.8 | 5.7 | 85 | 97 | 6.2 | 18.2 | 31 | 70.0 | 105.9 | 70.0 | 60.9 | 5.7 | 6.2 | 5.7 | 16.3 | 20 | 30 | 208/230-1-60
HP-2.5T | 50PSV030 | 950 | 0.300 | 26.2 | 20.1 | 76/65 | 56.4/55.8 | 6.1 | 85 | 97 | 2.5 | 16.6 | 32.7 | 70.0 | 101.9 | 70.0 | 61.1 | 6.1 | 2.5 | 5.9 | 16.9 | 20 | 30 | 208/230-1-60
HP-3.0T | 50PSV036 | 1,200 | 0.483 | 33.3 | 25.5 | 76/65 | 56.3/55.7 | 7.8 | 85 | 97 | 3.6 | 17.2 | 45 | 70.0 | 104.7 | 70.0 | 60.2 | 7.8 | 3.6 | 5.6 | 22.8 | 27 | 40 | 208/230-1-60
HP-3.5T | 50PSV042 | 1,400 | 0.500 | 39.4 | 31.9 | 76/65 | 57.2/56.7 | 9.1 | 85 | 97 | 4.7 | 18.2 | 47 | 70.0 | 97.7 | 70.0 | 61.2 | 9.1 | 4.7 | 6 | 21.4 | 25 | 40 | 208/230-1-60
HP-4.0T | 50PSV048 | 1,600 | 0.600 | 45.4 | 36.2 | 76/65 | 57.0/56.4 | 10.6 | 85 | 97 | 6.2 | 17.2 | 57.1 | 70.0 | 100 | 70.0 | 60.9 | 10.6 | 6.2 | 5.3 | 25.9 | 31 | 50 | 208/230-1-60
HP-5.0T | 50PSV060 | 2,000 | 0.525 | 55.8 | 41.8 | 76/65 | 56.6/55.7 | 13.3 | 85 | 97 | 9.3 | 16.2 | 79.2 | 70.0 | 106.6 | 70.0 | 59.9 | 13.3 | 9.3 | 5.7 | 32.6 | 39 | 60 | 208/230-1-60
HP-6.0T | 50PSV070 | 2,300 | 0.675 | 61.8 | 48.2 | 75/65 | 56.6/56.0 | 14.7 | 85 | 97 | 5.7 | 16.2 | 90.2 | 70.0 | 106.3 | 70.0 | 59.6 | 14.7 | 5.7 | 5.6 | 33.9 | 40 | 60 | 208/230-1-60
* EER - COP AT AHRI
- For 1/3 Ton or 3/4 Ton units, please contact your sales representative
- Units are also available in horizontal configuration

## 87-99
|  | Supply Fan |  | Heat Pump Cooling | [8 empty] | Heat Pump Heating | [7 empty] | Unit Electrical
Tag | Model | CFM | ESP | Net Total Capacity | Net Sensible Capacity | EAT DB/WB | LAT DB/WB | Fluid Flow | EWT | LWT | WPD | EER* | Total Capacity | EAT DB | LAT DB | EWT | LWT | Fluid Flow | WPD | COP* | Unit Amps | Unit MCA | Unit MFS | Unit Voltage
HP-1.0T | 50PSV012 | 400 | 0.450 | 11.3 | 8.3 | 76/65 | 56.4/55.4 | 2.7 | 87 | 99 | 2.8 | 14.9 | 15.7 | 70.0 | 107 | 70.0 | 60.6 | 2.7 | 9.5 | 5.1 | 5.56 | 7 | 15 | 208/230-1-60
HP-1.5T | 50PSV018 | 650 | 0.540 | 17.8 | 13.2 | 76/65 | 55.5/54.9 | 4.3 | 87 | 99 | 7.8 | 16.4 | 22.2 | 70.0 | 104.5 | 70.0 | 61.4 | 4.3 | 7.8 | 5.3 | 10.2 | 12 | 15 | 208/230-1-60
HP-2.0T | 50PSV024 | 800 | 0.500 | 24 | 17.8 | 76/65 | 55.4/54.9 | 5.7 | 87 | 99 | 6.2 | 18.2 | 31 | 70.0 | 105.9 | 70.0 | 60.9 | 5.7 | 6.2 | 5.7 | 16.3 | 20 | 30 | 208/230-1-60
HP-2.5T | 50PSV030 | 950 | 0.300 | 25.9 | 20 | 76/65 | 56.5/55.9 | 6.1 | 87 | 99 | 2.5 | 16.6 | 32.7 | 70.0 | 101.9 | 70.0 | 61.1 | 6.1 | 2.5 | 5.9 | 16.9 | 20 | 30 | 208/230-1-60
HP-3.0T | 50PSV036 | 1,200 | 0.483 | 33 | 25.4 | 76/65 | 56.4/55.8 | 7.8 | 87 | 99 | 3.6 | 17.2 | 45 | 70.0 | 104.7 | 70.0 | 60.2 | 7.8 | 3.6 | 5.6 | 22.8 | 27 | 40 | 208/230-1-60
HP-3.5T | 50PSV042 | 1,400 | 0.500 | 39 | 31.7 | 76/65 | 57.3/56.8 | 9.1 | 87 | 99 | 4.7 | 18.2 | 47 | 70.0 | 97.7 | 70.0 | 61.2 | 9.1 | 4.7 | 6 | 21.4 | 25 | 40 | 208/230-1-60
HP-4.0T | 50PSV048 | 1,600 | 0.600 | 44.9 | 36 | 76/65 | 57.1/56.5 | 10.6 | 87 | 99 | 6.2 | 17.2 | 57.1 | 70.0 | 100 | 70.0 | 60.9 | 10.6 | 6.2 | 5.3 | 25.9 | 31 | 50 | 208/230-1-60
HP-5.0T | 50PSV060 | 2,000 | 0.525 | 55 | 41.4 | 76/65 | 56.8/56.2 | 13.3 | 87 | 99 | 9.3 | 16.2 | 79.2 | 70.0 | 106.6 | 70.0 | 59.9 | 13.3 | 9.3 | 5.7 | 32.6 | 39 | 60 | 208/230-1-60
HP-6.0T | 50PSV070 | 2,300 | 0.675 | 60.9 | 47.8 | 75/65 | 56.4/55.4 | 14.7 | 87 | 99 | 5.7 | 16.2 | 90.2 | 70.0 | 106.3 | 70.0 | 59.6 | 14.7 | 5.7 | 5.6 | 33.9 | 40 | 60 | 208/230-1-60
* EER - COP AT AHRI
- For 1/3 Ton or 3/4 Ton units, please contact your sales representative
- Units are also available in horizontal configuration

## 88-100
|  | Supply Fan |  | Heat Pump Cooling | [8 empty] | Heat Pump Heating | [7 empty] | Unit Electrical
Tag | Model | CFM | ESP | Net Total Capacity | Net Sensible Capacity | EAT DB/WB | LAT DB/WB | Fluid Flow | EWT | LWT | WPD | EER* | Total Capacity | EAT DB | LAT DB | EWT | LWT | Fluid Flow | WPD | COP* | Unit Amps | Unit MCA | Unit MFS | Unit Voltage
HP-1.0T | 50PSV012 | 400 | 0.450 | 11.2 | 8.3 | 76/65 | 56.5/55.4 | 2.7 | 88 | 100 | 2.8 | 14.9 | 15.7 | 70.0 | 107 | 70.0 | 60.6 | 2.7 | 9.5 | 5.1 | 5.56 | 7 | 15 | 208/230-1-60
HP-1.5T | 50PSV018 | 650 | 0.540 | 17.7 | 13.2 | 76/65 | 55.4/55.0 | 4.3 | 88 | 100 | 7.8 | 16.4 | 22.2 | 70.0 | 104.5 | 70.0 | 61.4 | 4.3 | 7.8 | 5.3 | 10.2 | 12 | 15 | 208/230-1-60
HP-2.0T | 50PSV024 | 800 | 0.500 | 23.8 | 17.8 | 76/65 | 56.6/55.9 | 5.7 | 88 | 100 | 6.2 | 18.2 | 31 | 70.0 | 105.9 | 70.0 | 60.9 | 5.7 | 6.2 | 5.7 | 16.3 | 20 | 30 | 208/230-1-60
HP-2.5T | 50PSV030 | 950 | 0.300 | 25.8 | 19.9 | 76/65 | 56.4/55.9 | 6.1 | 88 | 100 | 2.5 | 16.6 | 32.7 | 70.0 | 101.9 | 70.0 | 61.1 | 6.1 | 2.5 | 5.9 | 16.9 | 20 | 30 | 208/230-1-60
HP-3.0T | 50PSV036 | 1,200 | 0.483 | 32.8 | 25.3 | 76/65 | 57.4/56.8 | 7.8 | 88 | 100 | 3.6 | 17.2 | 45 | 70.0 | 104.7 | 70.0 | 60.2 | 7.8 | 3.6 | 5.6 | 22.8 | 27 | 40 | 208/230-1-60
HP-3.5T | 50PSV042 | 1,400 | 0.500 | 38.7 | 31.7 | 76/65 | 57.1/56.6 | 9.1 | 88 | 100 | 4.7 | 18.2 | 47 | 70.0 | 97.7 | 70.0 | 61.2 | 9.1 | 4.7 | 6 | 21.4 | 25 | 40 | 208/230-1-60
HP-4.0T | 50PSV048 | 1,600 | 0.600 | 44.6 | 35.9 | 76/65 | 56.8/55.8 | 10.6 | 88 | 100 | 6.2 | 17.2 | 57.1 | 70.0 | 100 | 70.0 | 60.9 | 10.6 | 6.2 | 5.3 | 25.9 | 31 | 50 | 208/230-1-60
HP-5.0T | 50PSV060 | 2,000 | 0.525 | 55 | 41.4 | 76/65 | 56.8/56.2 | 13.3 | 88 | 100 | 9.3 | 16.2 | 79.2 | 70.0 | 106.6 | 70.0 | 59.9 | 13.3 | 9.3 | 5.7 | 32.6 | 39 | 60 | 208/230-1-60
HP-6.0T | 50PSV070 | 2,300 | 0.675 | 60.6 | 47.6 | 75/65 | 56.5/56.2 | 14.7 | 88 | 100 | 5.7 | 16.2 | 90.2 | 70.0 | 106.3 | 70.0 | 59.6 | 14.7 | 5.7 | 5.6 | 33.9 | 40 | 60 | 208/230-1-60
* EER - COP AT AHRI
- For 1/3 Ton or 3/4 Ton units, please contact your sales representative
- Units are also available in horizontal configuration