## 85-95
VERTICAL UNITS
|  | Supply Fan |  | Heat Pump Cooling | [8 empty] | Heat Pump Heating | [5 empty] | Unit Electrical 460 Volts |  |  |  | Unit Electrical 208/230 Volts
Tag | Model | CFM | ESP | Net Total Capacity | Net Sensible Capacity | EAT DB/WB | LAT DB/WB | Fluid Flow | EWT | LWT | WPD | EER* | Total Capacity | EAT DB | LAT DB | EWT | LWT | COP* | Unit Amps | Unit MCA | Unit MFS | Unit Voltage | Unit Amps | Unit MCA | Unit MFS | Unit Voltage
HP-6.0 Ton | 50VQP072 | 2,800 | 0.750 | 72.6 | 55.6 | 76/65 | 57.6/56.4 | 18.0 | 85.0 | 95.0 | 17.3 | 13.9 | 96.6 | 70.0 | 102.0 | 70.0 | 61.1 | 4.75 | 14 | 15 | 20 | 460-3-60 | 25.6 | 28 | 35 | 208/230-3-60
HP-8.0 Ton | 50VQP096 | 3,200 | 0.750 | 99.7 | 71.0 | 76/65 | 55.5/54.4 | 24.0 | 85.0 | 95 | 19.7 | 13.1 | 124.5 | 70.0 | 106.0 | 70.0 | 61.5 | 4.85 | 14.8 | 16 | 20 | 460-3-60 | 32.2 | 36 | 45 | 208/230-3-60
HP-10 Ton | 50VQP120 | 4,000 | 0.750 | 121.2 | 85.5 | 76/65 | 56.2/54.8 | 29.0 | 85.0 | 95 | 14.1 | 13.2 | 160.5 | 70.0 | 107.2 | 70.0 | 60.9 | 4.4 | 19.5 | 21 | 25 | 460-3-60 | 39.2 | 43 | 50 | 208/230-3-60
HP-12.5 Ton | 50VQP151 | 5,000 | 0.750 | 141.7 | 105.8 | 76/65 | 56.4/55.5 | 33.0 | 85.0 | 95 | 8.1 | 16 | 175.4 | 70.0 | 102.5 | 70.0 | 61.0 | 5.6 | 21.3 | 23 | 30 | 460-3-60 | 46.4 | 51 | 70 | 208/230-3-60
HP-15 Ton | 50VQP180 | 6,000 | 0.750 | 143.0 | 113.3 | 76/65 | 58.5/57.1 | 35.0 | 85.0 | 95 | 9.0 | 14.2 | 181.2 | 70.0 | 98.0 | 70.0 | 61.3 | 5 | 24 | 26 | 30 | 460-3-60 | 51.8 | 57 | 70 | 208/230-3-60
HP-18 Ton | 50VQP210 | 7,200 | 0.750 | 218.3 | 156.8 | 76/65 | 55.8/54.8 | 52.5 | 85.0 | 95 | 16.1 | 14.6 | 269.2 | 70.0 | 104.6 | 70.0 | 61.5 | 5.1 | 42.6 | 46 | 60 | 460-3-60 | 85.8 | 93 | 110 | 208/230-3-60
HP-20 Ton | 50VQP240 | 8,000 | 0.750 | 250.2 | 175.4 | 76/65 | 55.7/54.4 | 60.0 | 85.0 | 95 | 12.7 | 14.4 | 309.7 | 70.0 | 105.8 | 70.0 | 61.5 | 5.1 | 46.6 | 51 | 60 | 460-3-60 | 87.0 | 95 | 110 | 208/230-3-60
HP-25 Ton | 50VQP300 | 10,000 | 1.000 | 298.3 | 207.5 | 76/65 | 56.8/54.9 | 75.0 | 85.0 | 95 | 19.0 | 13 | 385.5 | 70.0 | 105.7 | 70.0 | 61.8 | 4.2 | 50.4 | 55 | 70 | 460-3-60 | 123.0 | 135 | 175 | 208/230-3-60
HP-30 Ton | 50VQP360 | 12,000 | 1.000 | 389.0 | 265.6 | 75/65 | 55.5/54.0 | 90.0 | 85.0 | 95 | 23.1 | 14.8 | 494.4 | 70.0 | 108.1 | 70.0 | 61.1 | 4.2 | 67 | 74 | 100 | 460-3-60 | 138.4 | 152 | 200 | 208/230-3-60
* EER - COP AT AHRI
HORIZONTAL UNITS
|  | Supply Fan |  | Heat Pump Cooling | [8 empty] | Heat Pump Heating | [5 empty] | Unit Electrical 460 Volts |  |  |  | Unit Electrical 208/230 Volts
Tag | Model | CFM | ESP | Net Total Capacity | Net Sensible Capacity | EAT DB/WB | LAT DB/WB | Fluid Flow | EWT | LWT | WPD | EER* | Total Capacity | EAT DB | LAT DB | EWT | LWT | COP* | Unit Amps | Unit MCA | Unit MFS | Unit Voltage | Unit Amps | Unit MCA | Unit MFS | Unit Voltage
HP-6.0 Ton | 50HQP072 | 2,800 | 0.750 | 72.6 | 55.6 | 76/65 | 57.6/56.4 | 18.0 | 85.0 | 95.0 | 17.3 | 13.9 | 96.6 | 70.0 | 102.0 | 70.0 | 61.1 | 4.75 | 14 | 15 | 20 | 460-3-60 | 25.6 | 28 | 35 | 208/230-3-60
HP-8.0 Ton | 50HQP096 | 3,200 | 0.750 | 99.7 | 71.0 | 76/65 | 55.5/54.4 | 24.0 | 85.0 | 95 | 19.7 | 13.1 | 124.5 | 70.0 | 106.0 | 70.0 | 61.5 | 4.85 | 14.8 | 16 | 20 | 460-3-60 | 32.2 | 36 | 45 | 208/230-3-60
HP-10 Ton | 50HQP120 | 4,000 | 0.750 | 121.2 | 85.5 | 76/65 | 56.2/54.8 | 29.0 | 85.0 | 95 | 14.1 | 13.2 | 160.5 | 70.0 | 107.2 | 70.0 | 60.9 | 4.4 | 19.5 | 21 | 25 | 460-3-60 | 39.2 | 43 | 50 | 208/230-3-60
HP-12.5 Ton | 50HQP150 | 5,000 | 0.750 | 141.7 | 105.8 | 76/65 | 56.4/55.5 | 33.0 | 85.0 | 95 | 8.1 | 16 | 175.4 | 70.0 | 102.5 | 70.0 | 61.0 | 5.6 | 21.3 | 23 | 30 | 460-3-60 | 46.4 | 51 | 70 | 208/230-3-60
HP-15 Ton | 50HQP180 | 6,000 | 0.750 | 143.0 | 113.3 | 76/65 | 58.5/57.1 | 35.0 | 85.0 | 95 | 9.0 | 14.2 | 181.2 | 70.0 | 98.0 | 70.0 | 61.3 | 5 | 24 | 26 | 30 | 460-3-60 | 51.8 | 57 | 70 | 208/230-3-60
HP-20 Ton | 50HQP240 | 8,000 | 0.750 | 250.2 | 175.4 | 76/65 | 56.8/54.9 | 60.0 | 85.0 | 95 | 12.7 | 14.4 | 309.7 | 70.0 | 105.8 | 70.0 | 61.5 | 5.1 | 46.6 | 51 | 60 | 460-3-60 | 87.0 | 95 | 110 | 208/230-3-60
* EER - COP AT AHRI

## 87-97
VERTICAL UNITS
|  | Supply Fan |  | Heat Pump Cooling | [8 empty] | Heat Pump Heating | [5 empty] | Unit Electrical 460 Volts |  |  |  | Unit Electrical 208/230 Volts
Tag | Model | CFM | ESP | Net Total Capacity | Net Sensible Capacity | EAT DB/WB | LAT DB/WB | Fluid Flow | EWT | LWT | WPD | EER* | Total Capacity | EAT DB | LAT DB | EWT | LWT | COP* | Unit Amps | Unit MCA | Unit MFS | Unit Voltage | Unit Amps | Unit MCA | Unit MFS | Unit Voltage
HP-6.0 Ton | 50VQP072 | 2,800 | 0.750 | 71.5 | 55.1 | 76/65 | 57.8/56.5 | 18.0 | 87 | 97 | 17.3 | 13.9 | 85.5 | 70.0 | 102.0 | 70.0 | 61.1 | 4.75 | 14 | 15 | 20 | 460-3-60 | 25.6 | 28 | 35 | 208/230-3-60
HP-8.0 Ton | 50VQP096 | 3,200 | 0.750 | 98.6 | 70.6 | 76/65 | 55.6/54.6 | 24.0 | 87 | 97 | 19.7 | 13.1 | 116.8 | 70.0 | 106.0 | 70.0 | 61.5 | 4.85 | 14.8 | 16 | 20 | 460-3-60 | 32.2 | 36 | 45 | 208/230-3-60
HP-10 Ton | 50VQP120 | 4,000 | 0.750 | 119.9 | 85.0 | 76/65 | 56.3/54.9 | 29.0 | 87 | 97 | 14.1 | 13.2 | 142.7 | 70.0 | 107.2 | 70.0 | 60.9 | 4.4 | 19.5 | 21 | 25 | 460-3-60 | 39.2 | 43 | 50 | 208/230-3-60
HP-12.5 Ton | 50VQP151 | 5,000 | 0.750 | 140.0 | 105.2 | 76/65 | 56.5/55.6 | 33.0 | 87 | 97 | 8.1 | 16 | 164.0 | 70.0 | 102.5 | 70.0 | 61.0 | 5.6 | 21.3 | 23 | 30 | 460-3-60 | 46.4 | 51 | 70 | 208/230-3-60
HP-15 Ton | 50VQP180 | 6,000 | 0.750 | 141.4 | 112.8 | 76/65 | 58.6/57.2 | 35.0 | 87 | 97 | 9.0 | 14.2 | 165.2 | 70.0 | 98.0 | 70.0 | 61.3 | 5 | 24 | 26 | 30 | 460-3-60 | 51.8 | 57 | 70 | 208/230-3-60
HP-18 Ton | 50VQP210 | 7,200 | 0.750 | 216.1 | 156.0 | 76/65 | 55.9/54.9 | 52.5 | 87 | 97 | 16.1 | 14.6 | 255.7 | 70.0 | 104.6 | 70.0 | 61.5 | 5.1 | 42.6 | 46 | 60 | 460-3-60 | 85.8 | 93 | 110 | 208/230-3-60
HP-20 Ton | 50VQP240 | 8,000 | 0.750 | 247.7 | 174.4 | 76/65 | 55.8/54.5 | 60.0 | 87 | 97 | 12.7 | 14.4 | 291.7 | 70.0 | 105.8 | 70.0 | 61.5 | 5.1 | 46.6 | 51 | 60 | 460-3-60 | 87.0 | 95 | 110 | 208/230-3-60
HP-25 Ton | 50VQP300 | 10,000 | 1.000 | 295.3 | 206.0 | 76/65 | 56.9/55.1 | 75.0 | 87 | 97 | 19.0 | 13 | 353.9 | 70.0 | 105.7 | 70.0 | 61.8 | 4.2 | 50.4 | 55 | 70 | 460-3-60 | 123.0 | 135 | 175 | 208/230-3-60
HP-30 Ton | 50VQP360 | 12,000 | 1.000 | 385.2 | 263.8 | 75/65 | 55.6/54.1 | 90.0 | 87 | 97 | 23.1 | 14.8 | 455.8 | 70.0 | 108.1 | 70.0 | 61.1 | 4.2 | 67 | 74 | 100 | 460-3-60 | 138.4 | 152 | 200 | 208/230-3-60
* EER - COP AT AHRI
HORIZONTAL UNITS
|  | Supply Fan |  | Heat Pump Cooling | [8 empty] | Heat Pump Heating | [5 empty] | Unit Electrical 460 Volts |  |  |  | Unit Electrical 208/230 Volts
Tag | Model | CFM | ESP | Net Total Capacity | Net Sensible Capacity | EAT DB/WB | LAT DB/WB | Fluid Flow | EWT | LWT | WPD | EER* | Total Capacity | EAT DB | LAT DB | EWT | LWT | COP* | Unit Amps | Unit MCA | Unit MFS | Unit Voltage | Unit Amps | Unit MCA | Unit MFS | Unit Voltage
HP-6.0 Ton | 50HQP072 | 2,800 | 0.750 | 71.5 | 55.1 | 76/65 | 57.8/56.5 | 18.0 | 87 | 97 | 17.3 | 13.9 | 85.5 | 70.0 | 102.0 | 70.0 | 61.1 | 4.75 | 14 | 15 | 20 | 460-3-60 | 25.6 | 28 | 35 | 208/230-3-60
HP-8.0 Ton | 50HQP096 | 3,200 | 0.750 | 98.6 | 70.6 | 76/65 | 55.6/54.6 | 24.0 | 87 | 97 | 19.7 | 13.1 | 116.8 | 70.0 | 106.0 | 70.0 | 61.5 | 4.85 | 14.8 | 16 | 20 | 460-3-60 | 32.2 | 36 | 45 | 208/230-3-60
HP-10 Ton | 50HQP120 | 4,000 | 0.750 | 119.9 | 85.0 | 76/65 | 56.3/54.9 | 29.0 | 87 | 97 | 14.1 | 13.2 | 142.7 | 70.0 | 107.2 | 70.0 | 60.9 | 4.4 | 19.5 | 21 | 25 | 460-3-60 | 39.2 | 43 | 50 | 208/230-3-60
HP-12.5 Ton | 50HQP150 | 5,000 | 0.750 | 140.0 | 105.2 | 76/65 | 56.5/55.6 | 33.0 | 87 | 97 | 8.1 | 16 | 164.0 | 70.0 | 102.5 | 70.0 | 61.0 | 5.6 | 21.3 | 23 | 30 | 460-3-60 | 46.4 | 51 | 70 | 208/230-3-60
HP-15 Ton | 50HQP180 | 6,000 | 0.750 | 141.4 | 112.8 | 76/65 | 58.6/57.2 | 35.0 | 87 | 97 | 9.0 | 14.2 | 165.2 | 70.0 | 98.0 | 70.0 | 61.3 | 5 | 24 | 26 | 30 | 460-3-60 | 51.8 | 57 | 70 | 208/230-3-60
HP-20 Ton | 50HQP240 | 8,000 | 0.750 | 247.7 | 174.4 | 76/65 | 55.8/54.5 | 60.0 | 87 | 97 | 12.7 | 14.4 | 291.7 | 70.0 | 105.8 | 70.0 | 61.5 | 5.1 | 46.6 | 51 | 60 | 460-3-60 | 87.0 | 95 | 110 | 208/230-3-60
* EER - COP AT AHRI

## 85-97
VERTICAL UNITS
|  | Supply Fan |  | Heat Pump Cooling | [8 empty] | Heat Pump Heating | [5 empty] | Unit Electrical 460 Volts |  |  |  | Unit Electrical 208/230 Volts
Tag | Model | CFM | ESP | Net Total Capacity | Net Sensible Capacity | EAT DB/WB | LAT DB/WB | Fluid Flow | EWT | LWT | WPD | EER* | Total Capacity | EAT DB | LAT DB | EWT | LWT | COP* | Unit Amps | Unit MCA | Unit MFS | Unit Voltage | Unit Amps | Unit MCA | Unit MFS | Unit Voltage
HP-6.0 Ton | 50VQP072 | 2,800 | 0.750 | 70.9 | 55.0 | 76/65 | 57.8/56.6 | 14.0 | 85 | 97 | 11.0 | 13.9 | 93.5 | 70.0 | 100.9 | 70.0 | 59.0 | 4.75 | 14 | 15 | 20 | 460-3-60 | 25.6 | 28 | 35 | 208/230-3-60
HP-8.0 Ton | 50VQP096 | 3,200 | 0.750 | 97.8 | 70.3 | 76/65 | 55.7/54.7 | 19.0 | 85 | 97 | 12.9 | 13.1 | 121.0 | 70.0 | 105.0 | 70.0 | 59.6 | 4.85 | 14.8 | 16 | 20 | 460-3-60 | 32.2 | 36 | 45 | 208/230-3-60
HP-10 Ton | 50VQP120 | 4,000 | 0.750 | 117.0 | 84.7 | 76/65 | 56.4/55.2 | 23.0 | 85 | 97 | 9.3 | 13.2 | 155.4 | 70.0 | 106.0 | 70.0 | 59.0 | 4.4 | 19.5 | 21 | 25 | 460-3-60 | 39.2 | 43 | 50 | 208/230-3-60
HP-12.5 Ton | 50VQP151 | 5,000 | 0.750 | 137.1 | 104.5 | 76/65 | 56.6/55.8 | 27.0 | 85 | 97 | 5.7 | 16 | 170.6 | 70.0 | 101.6 | 70.0 | 59.4 | 5.6 | 21.3 | 23 | 30 | 460-3-60 | 46.4 | 51 | 70 | 208/230-3-60
HP-15 Ton | 50VQP180 | 6,000 | 0.750 | 138.4 | 111.3 | 76/65 | 58.8/57.4 | 27.0 | 85 | 97 | 5.7 | 14.2 | 174.5 | 70.0 | 96.9 | 70.0 | 59.2 | 5 | 24 | 26 | 30 | 460-3-60 | 51.8 | 57 | 70 | 208/230-3-60
HP-18 Ton | 50VQP210 | 7,200 | 0.750 | 211.8 | 155.4 | 76/65 | 56.0/55.1 | 42.0 | 85 | 97 | 10.8 | 14.6 | 260.5 | 70.0 | 103.5 | 70.0 | 59.7 | 5.1 | 42.6 | 46 | 60 | 460-3-60 | 85.8 | 93 | 110 | 208/230-3-60
HP-20 Ton | 50VQP240 | 8,000 | 0.750 | 241.6 | 173.8 | 76/65 | 55.9/54.8 | 48.0 | 85 | 97 | 8.5 | 14.4 | 299.2 | 70.0 | 104.6 | 70.0 | 59.7 | 5.1 | 46.6 | 51 | 60 | 460-3-60 | 87.0 | 95 | 110 | 208/230-3-60
HP-25 Ton | 50VQP300 | 10,000 | 1.000 | 286.6 | 205.1 | 76/65 | 57.0/55.4 | 58.0 | 85 | 97 | 11.9 | 13 | 373.3 | 70.0 | 104.6 | 70.0 | 59.7 | 4.2 | 50.4 | 55 | 70 | 460-3-60 | 123.0 | 135 | 175 | 208/230-3-60
HP-30 Ton | 50VQP360 | 12,000 | 1.000 | 377.6 | 263.3 | 75/65 | 55.7/54.3 | 75.0 | 85 | 97 | 16.6 | 14.8 | 481.4 | 70.0 | 107.1 | 70.0 | 59.7 | 4.2 | 67 | 74 | 100 | 460-3-60 | 138.4 | 152 | 200 | 208/230-3-60
* EER - COP AT AHRI
HORIZONTAL UNITS
|  | Supply Fan |  | Heat Pump Cooling | [8 empty] | Heat Pump Heating | [5 empty] | Unit Electrical 460 Volts |  |  |  | Unit Electrical 208/230 Volts
Tag | Model | CFM | ESP | Net Total Capacity | Net Sensible Capacity | EAT DB/WB | LAT DB/WB | Fluid Flow | EWT | LWT | WPD | EER* | Total Capacity | EAT DB | LAT DB | EWT | LWT | COP* | Unit Amps | Unit MCA | Unit MFS | Unit Voltage | Unit Amps | Unit MCA | Unit MFS | Unit Voltage
HP-6.0 Ton | 50HQP072 | 2,800 | 0.750 | 70.9 | 55.0 | 76/65 | 57.8/56.6 | 14.0 | 85 | 97 | 11.0 | 13.9 | 93.5 | 70.0 | 100.9 | 70.0 | 59.0 | 4.75 | 14 | 15 | 20 | 460-3-60 | 25.6 | 28 | 35 | 208/230-3-60
HP-8.0 Ton | 50HQP096 | 3,200 | 0.750 | 97.8 | 70.3 | 76/65 | 55.7/54.7 | 19.0 | 85 | 97 | 12.9 | 13.1 | 121.0 | 70.0 | 105.0 | 70.0 | 59.6 | 4.85 | 14.8 | 16 | 20 | 460-3-60 | 32.2 | 36 | 45 | 208/230-3-60
HP-10 Ton | 50HQP120 | 4,000 | 0.750 | 117.0 | 84.7 | 76/65 | 56.4/55.2 | 23.0 | 85 | 97 | 9.3 | 13.2 | 155.4 | 70.0 | 106.0 | 70.0 | 59.0 | 4.4 | 19.5 | 21 | 25 | 460-3-60 | 39.2 | 43 | 50 | 208/230-3-60
HP-12.5 Ton | 50HQP150 | 5,000 | 0.750 | 137.1 | 104.5 | 76/65 | 56.6/55.8 | 27.0 | 85 | 97 | 5.7 | 16 | 170.6 | 70.0 | 101.6 | 70.0 | 59.4 | 5.6 | 21.3 | 23 | 30 | 460-3-60 | 46.4 | 51 | 70 | 208/230-3-60
HP-15 Ton | 50HQP180 | 6,000 | 0.750 | 138.4 | 111.3 | 76/65 | 58.8/57.4 | 27.0 | 85 | 97 | 5.7 | 14.2 | 174.5 | 70.0 | 96.9 | 70.0 | 59.2 | 5 | 24 | 26 | 30 | 460-3-60 | 51.8 | 57 | 70 | 208/230-3-60
HP-20 Ton | 50HQP240 | 8,000 | 0.750 | 241.6 | 173.8 | 76/65 | 55.9/54.8 | 48.0 | 85 | 97 | 8.5 | 14.4 | 299.2 | 70.0 | 104.6 | 70.0 | 59.7 | 5.1 | 46.6 | 51 | 60 | 460-3-60 | 87.0 | 95 | 110 | 208/230-3-60
* EER - COP AT AHRI

## 87-99
VERTICAL UNITS
|  | Supply Fan |  | Heat Pump Cooling | [8 empty] | Heat Pump Heating | [5 empty] | Unit Electrical 460 Volts |  |  |  | Unit Electrical 208/230 Volts
Tag | Model | CFM | ESP | Net Total Capacity | Net Sensible Capacity | EAT DB/WB | LAT DB/WB | Fluid Flow | EWT | LWT | WPD | EER* | Total Capacity | EAT DB | LAT DB | EWT | LWT | COP* | Unit Amps | Unit MCA | Unit MFS | Unit Voltage | Unit Amps | Unit MCA | Unit MFS | Unit Voltage
HP-6.0 Ton | 50VQP072 | 2,800 | 0.750 | 69.7 | 54.6 | 76/65 | 58.0/56.7 | 14.0 | 87 | 99 | 11.0 | 13.9 | 93.5 | 70.0 | 100.9 | 70.0 | 59.0 | 4.75 | 14 | 15 | 20 | 460-3-60 | 25.6 | 28 | 35 | 208/230-3-60
HP-8.0 Ton | 50VQP096 | 3,200 | 0.750 | 96.5 | 69.9 | 76/65 | 55.8/54.8 | 19.0 | 87 | 99 | 12.9 | 13.1 | 121.0 | 70.0 | 105.0 | 70.0 | 59.6 | 4.85 | 14.8 | 16 | 20 | 460-3-60 | 32.2 | 36 | 45 | 208/230-3-60
HP-10 Ton | 50VQP120 | 4,000 | 0.750 | 114.9 | 84.1 | 76/65 | 56.5/55.3 | 23.0 | 87 | 99 | 9.3 | 13.2 | 155.4 | 70.0 | 106.0 | 70.0 | 59.0 | 4.4 | 19.5 | 21 | 25 | 460-3-60 | 39.2 | 43 | 50 | 208/230-3-60
HP-12.5 Ton | 50VQP151 | 5,000 | 0.750 | 134.4 | 104.1 | 76/65 | 56.7/56.0 | 27.0 | 87 | 99 | 5.7 | 16 | 170.6 | 70.0 | 101.6 | 70.0 | 59.4 | 5.6 | 21.3 | 23 | 30 | 460-3-60 | 46.4 | 51 | 70 | 208/230-3-60
HP-15 Ton | 50VQP180 | 6,000 | 0.750 | 136.2 | 110.8 | 76/65 | 58.9/57.5 | 27.0 | 87 | 99 | 5.7 | 14.2 | 174.5 | 70.0 | 96.9 | 70.0 | 59.2 | 5 | 24 | 26 | 30 | 460-3-60 | 51.8 | 57 | 70 | 208/230-3-60
HP-18 Ton | 50VQP210 | 7,200 | 0.750 | 208.5 | 154.5 | 76/65 | 56.1/55.3 | 42.0 | 87 | 99 | 10.8 | 14.6 | 260.5 | 70.0 | 103.5 | 70.0 | 59.7 | 5.1 | 42.6 | 46 | 60 | 460-3-60 | 85.8 | 93 | 110 | 208/230-3-60
HP-20 Ton | 50VQP240 | 8,000 | 0.750 | 237.4 | 172.9 | 76/65 | 56.0/55.0 | 48.0 | 87 | 99 | 8.5 | 14.4 | 299.2 | 70.0 | 104.6 | 70.0 | 59.7 | 5.1 | 46.6 | 51 | 60 | 460-3-60 | 87.0 | 95 | 110 | 208/230-3-60
HP-25 Ton | 50VQP300 | 10,000 | 1.000 | 281.1 | 203.8 | 76/65 | 57.1/55.6 | 58.0 | 87 | 99 | 11.9 | 13 | 373.3 | 70.0 | 104.6 | 70.0 | 59.7 | 4.2 | 50.4 | 55 | 70 | 460-3-60 | 123.0 | 135 | 175 | 208/230-3-60
HP-30 Ton | 50VQP360 | 12,000 | 1.000 | 371.5 | 261.6 | 75/65 | 55.8/54.5 | 75.0 | 87 | 99 | 16.6 | 14.8 | 481.4 | 70.0 | 107.1 | 70.0 | 59.7 | 4.2 | 67 | 74 | 100 | 460-3-60 | 138.4 | 152 | 200 | 208/230-3-60
* EER - COP AT AHRI
HORIZONTAL UNITS
|  | Supply Fan |  | Heat Pump Cooling | [8 empty] | Heat Pump Heating | [5 empty] | Unit Electrical 460 Volts |  |  |  | Unit Electrical 208/230 Volts
Tag | Model | CFM | ESP | Net Total Capacity | Net Sensible Capacity | EAT DB/WB | LAT DB/WB | Fluid Flow | EWT | LWT | WPD | EER* | Total Capacity | EAT DB | LAT DB | EWT | LWT | COP* | Unit Amps | Unit MCA | Unit MFS | Unit Voltage | Unit Amps | Unit MCA | Unit MFS | Unit Voltage
HP-6.0 Ton | 50HQP072 | 2,800 | 0.750 | 69.7 | 54.6 | 76/65 | 58.0/56.7 | 14.0 | 87 | 99 | 11.0 | 13.9 | 93.5 | 70.0 | 100.9 | 70.0 | 59.0 | 4.75 | 14 | 15 | 20 | 460-3-60 | 25.6 | 28 | 35 | 208/230-3-60
HP-8.0 Ton | 50HQP096 | 3,200 | 0.750 | 96.5 | 69.9 | 76/65 | 55.8/54.8 | 19.0 | 87 | 99 | 12.9 | 13.1 | 121.0 | 70.0 | 105.0 | 70.0 | 59.6 | 4.85 | 14.8 | 16 | 20 | 460-3-60 | 32.2 | 36 | 45 | 208/230-3-60
HP-10 Ton | 50HQP120 | 4,000 | 0.750 | 114.9 | 84.1 | 76/65 | 56.5/55.3 | 23.0 | 87 | 99 | 9.3 | 13.2 | 155.4 | 70.0 | 106.0 | 70.0 | 59.0 | 4.4 | 19.5 | 21 | 25 | 460-3-60 | 39.2 | 43 | 50 | 208/230-3-60
HP-12.5 Ton | 50HQP150 | 5,000 | 0.750 | 134.4 | 104.1 | 76/65 | 56.7/56.0 | 27.0 | 87 | 99 | 5.7 | 16 | 170.6 | 70.0 | 101.6 | 70.0 | 59.4 | 5.6 | 21.3 | 23 | 30 | 460-3-60 | 46.4 | 51 | 70 | 208/230-3-60
HP-15 Ton | 50HQP180 | 6,000 | 0.750 | 136.2 | 110.8 | 76/65 | 58.9/57.5 | 27.0 | 87 | 99 | 5.7 | 14.2 | 174.5 | 70.0 | 96.9 | 70.0 | 59.2 | 5 | 24 | 26 | 30 | 460-3-60 | 51.8 | 57 | 70 | 208/230-3-60
HP-20 Ton | 50HQP240 | 8,000 | 0.750 | 234.3 | 171.4 | 76/65 | 56.2/55.1 | 48.0 | 87 | 99 | 8.5 | 14.4 | 299.2 | 70.0 | 104.6 | 70.0 | 59.7 | 5.1 | 46.6 | 51 | 60 | 460-3-60 | 87.0 | 95 | 110 | 208/230-3-60
* EER - COP AT AHRI

## 88-100
VERTICAL UNITS
|  | Supply Fan |  | Heat Pump Cooling | [8 empty] | Heat Pump Heating | [5 empty] | Unit Electrical 460 Volts |  |  |  | Unit Electrical 208/230 Volts
Tag | Model | CFM | ESP | Net Total Capacity | Net Sensible Capacity | EAT DB/WB | LAT DB/WB | Fluid Flow | EWT | LWT | WPD | EER* | Total Capacity | EAT DB | LAT DB | EWT | LWT | COP* | Unit Amps | Unit MCA | Unit MFS | Unit Voltage | Unit Amps | Unit MCA | Unit MFS | Unit Voltage
HP-6.0 Ton | 50VQP072 | 2,800 | 0.750 | 69.1 | 54.3 | 76/65 | 58.0/56.8 | 14.0 | 88 | 100 | 11.0 | 13.9 | 93.5 | 70.0 | 100.9 | 70.0 | 59.0 | 4.75 | 14 | 15 | 20 | 460-3-60 | 25.6 | 28 | 35 | 208/230-3-60
HP-8.0 Ton | 50VQP096 | 3,200 | 0.750 | 95.9 | 69.7 | 76/65 | 55.8/54.9 | 19.0 | 88 | 100 | 12.9 | 13.1 | 121.0 | 70.0 | 105.0 | 70.0 | 59.6 | 4.85 | 14.8 | 16 | 20 | 460-3-60 | 32.2 | 36 | 45 | 208/230-3-60
HP-10 Ton | 50VQP120 | 4,000 | 0.750 | 114.4 | 84.3 | 76/65 | 56.5/55.4 | 23.0 | 88 | 100 | 9.3 | 13.2 | 154.9 | 70.0 | 105.9 | 70.0 | 59.0 | 4.4 | 19.5 | 21 | 25 | 460-3-60 | 39.2 | 43 | 50 | 208/230-3-60
HP-12.5 Ton | 50VQP151 | 5,000 | 0.750 | 132.5 | 103.4 | 76/65 | 56.9/56.2 | 27.0 | 88 | 100 | 5.7 | 16 | 171.2 | 70.0 | 101.7 | 70.0 | 59.4 | 5.6 | 21.3 | 23 | 30 | 460-3-60 | 46.4 | 51 | 70 | 208/230-3-60
HP-15 Ton | 50VQP180 | 6,000 | 0.750 | 134.5 | 109.8 | 76/65 | 59.0/57.6 | 27.0 | 88 | 100 | 5.7 | 14.2 | 175.2 | 70.0 | 97.0 | 70.0 | 59.2 | 5 | 24 | 26 | 30 | 460-3-60 | 51.8 | 57 | 70 | 208/230-3-60
HP-18 Ton | 50VQP210 | 7,200 | 0.750 | 205.9 | 153.2 | 76/65 | 56.3/55.4 | 42.0 | 88 | 100 | 10.8 | 14.6 | 261.4 | 70.0 | 103.6 | 70.0 | 59.7 | 5.1 | 42.6 | 46 | 60 | 460-3-60 | 85.8 | 93 | 110 | 208/230-3-60
HP-20 Ton | 50VQP240 | 8,000 | 0.750 | 234.3 | 171.4 | 76/65 | 56.2/55.1 | 48.0 | 88 | 100 | 8.5 | 14.4 | 300.3 | 70.0 | 104.8 | 70.0 | 59.7 | 5.1 | 46.6 | 51 | 60 | 460-3-60 | 87.0 | 95 | 110 | 208/230-3-60
HP-25 Ton | 50VQP300 | 10,000 | 1.000 | 278.4 | 203.1 | 76/65 | 57.2/55.7 | 58.0 | 88 | 100 | 11.9 | 13 | 373.3 | 70.0 | 104.6 | 70.0 | 59.7 | 4.2 | 50.4 | 55 | 70 | 460-3-60 | 123.0 | 135 | 175 | 208/230-3-60
HP-30 Ton | 50VQP360 | 12,000 | 1.000 | 368.5 | 260.8 | 75/65 | 55.9/54.6 | 75.0 | 88 | 100 | 16.6 | 14.8 | 481.4 | 70.0 | 107.1 | 70.0 | 59.7 | 4.2 | 67 | 74 | 100 | 460-3-60 | 138.4 | 152 | 200 | 208/230-3-60
* EER - COP AT AHRI
HORIZONTAL UNITS
|  | Supply Fan |  | Heat Pump Cooling | [8 empty] | Heat Pump Heating | [5 empty] | Unit Electrical 460 Volts |  |  |  | Unit Electrical 208/230 Volts
Tag | Model | CFM | ESP | Net Total Capacity | Net Sensible Capacity | EAT DB/WB | LAT DB/WB | Fluid Flow | EWT | LWT | WPD | EER* | Total Capacity | EAT DB | LAT DB | EWT | LWT | COP* | Unit Amps | Unit MCA | Unit MFS | Unit Voltage | Unit Amps | Unit MCA | Unit MFS | Unit Voltage
HP-6.0 Ton | 50HQP072 | 2,800 | 0.750 | 69.1 | 54.3 | 76/65 | 58.0/56.8 | 14.0 | 88 | 100 | 11.0 | 13.9 | 93.5 | 70.0 | 100.9 | 70.0 | 59.0 | 4.75 | 14 | 15 | 20 | 460-3-60 | 25.6 | 28 | 35 | 208/230-3-60
HP-8.0 Ton | 50HQP096 | 3,200 | 0.750 | 95.9 | 69.7 | 76/65 | 55.8/54.9 | 19.0 | 88 | 100 | 12.9 | 13.1 | 121.0 | 70.0 | 105.0 | 70.0 | 59.6 | 4.85 | 14.8 | 16 | 20 | 460-3-60 | 32.2 | 36 | 45 | 208/230-3-60
HP-10 Ton | 50HQP120 | 4,000 | 0.750 | 114.4 | 84.3 | 76/65 | 56.5/55.4 | 23.0 | 88 | 100 | 9.3 | 13.2 | 154.9 | 70.0 | 105.9 | 70.0 | 59.0 | 4.4 | 19.5 | 21 | 25 | 460-3-60 | 39.2 | 43 | 50 | 208/230-3-60
HP-12.5 Ton | 50HQP150 | 5,000 | 0.750 | 132.5 | 103.4 | 76/65 | 56.9/56.2 | 27.0 | 88 | 100 | 5.7 | 16 | 171.2 | 70.0 | 101.7 | 70.0 | 59.4 | 5.6 | 21.3 | 23 | 30 | 460-3-60 | 46.4 | 51 | 70 | 208/230-3-60
HP-15 Ton | 50HQP180 | 6,000 | 0.750 | 134.5 | 109.8 | 76/65 | 59.0/57.6 | 27.0 | 88 | 100 | 5.7 | 14.2 | 175.2 | 70.0 | 97.0 | 70.0 | 59.2 | 5 | 24 | 26 | 30 | 460-3-60 | 51.8 | 57 | 70 | 208/230-3-60
HP-20 Ton | 50HQP240 | 8,000 | 0.750 | 234.3 | 171.4 | 76/65 | 56.2/55.1 | 48.0 | 88 | 100 | 8.5 | 14.4 | 300.3 | 70.0 | 104.8 | 70.0 | 59.7 | 5.1 | 46.6 | 51 | 60 | 460-3-60 | 87.0 | 95 | 110 | 208/230-3-60
* EER - COP AT AHRI