## VALENT VX-SERIES @ 208-3-60
VALENT VX- SERIES 100% OUTSIDE AIR DX ROOFTOP PACKAGED UNITS @ 208/3/60
NOM TONS | 7.5 | 12.5 | 15 | 17.5 | 20 | 25 | 30
MODEL NUMBER | VX-112-7.5 | VX-112-12.5 | VX-212-15 | VX-12-17.5 | VX-212-20 | VX-212-25 | VX-212-30
AMBIENT TEMP. | 95 | 95 | 95 | 95 | 95 | 95 | 95
REFRIGERANT | R-410A | R-410A | R-410A | R-410A | R-410A | R-410A | R-410A
TOTAL / SENS. (MBH) @ 91.8 / 80.2 | 94.5 / 41.1 | 151.7 / 65.8 | 191.5 / 83.3 | 230.5 / 100.5 | 269.5 / 117.9 | 331.2 / 144.1 | 371.3 / 161.8
LEAVING DB / WB (F) | 54.6 / 54.6 | 52.1 / 52.1 | 54.2 / 54.2 | 55.5 / 55.4 | 56.3 / 56.3 | 54.6 / 54.6 | 55.3 / 55.2
HOT GAS REHEAT (MBH) | 43.4 | 57.4 | 79.2 | 90.4 | 101.1 | 121.4 | 135.7
TOTAL CFM | 1000 | 1500 | 2000 | 2500 | 3000 | 3500 | 4000
ESP (W.G.) | 1.00" | 1.00" | 1.00" | 1.00" | 1.00" | 1.00" | 1.00"
COMPR. QTY. / TYPE | 1 / INVERTER SCROLL | 1 / INVERTER SCROLL | 2 / INVERTER SCROLL | 2 / INVERTER SCROLL | 2 / INVERTER SCROLL | 2 / INVERTER SCROLL | 2 / INVERTER SCROLL
BHP / HP MOTOR | 0.287 / 1.0 | 0.467 / 1.0 | 0.745 / 1.0 | 0.759 / 3.0 | 0.97 / 3.0 | 1.228 / 3.0 | 1.545 / 3.0
MCA | 46.6 | 48.8 | 111.3 | 111.3 | 111.3 | 132.1 | 154
MOCP | 50 | 60 | 125 | 125 | 125 | 175 | 175
DIMENSIONS (H, W, L) (IN.) | 65 X 53 X 99 | 60 X 53 X 99 | 76 X 68 X 109 | 76 X 68 X 109 | 76 X 68 X 109 | 76 X 68 X 109 | 76 X 68 X 109
WEIGHT (LBS.) | 2311 | 2444 | 3338 | 3425 | 3546 | 3638 | 3668
FILTERS / QTY. - SIZE (IN.) 2" PLEATED - MERV 8 | 4 - 20 X 20 X 2 | 4 - 20 X 20 X 2 | 8 - 16 X 25 X 2 | 8 - 16 X 25 X 2 | 8 - 16 X 25 X 2 | 8 - 16 X 25 X 2 | 8 - 16 X 25 X 2
HEATER KW @ 208 V | 12.3 | 12.3 | 28.7 | 28.7 | 28.7 | 32.8 | 41
HEATER AMPS | 34.1 | 34.1 | 79.7 | 79.7 | 79.7 | 91 | 113.8
SCHEDULE NOTES:
1) BASIS OF DESIGN IS VALENT PRODUCTS.
2) PROVIDE FACTORY-INSTALLED MODULATING HOT GAS REHEAT.
3) PROVIDE 2" DOUBLE WALL, R-13 INTERNAL INSULATION.
4) PROVIDE ELECTRIC HEATER WITH SCR CONTROLLER AND SINGLE POINT POWER.
5) PROVIDE FACTORY-INSTALLED SUPPLY FAN VFD CONTROLLER, PREMIUM EFFICIENCY MOTOR.
6) PROVIDE FACTORY-INSTALLED ELECTRO-FIN COATED CONDENSER AND EVAPORATOR COILS.
7) PROVIDE FACTORY-INSTALLED UNIT MOUNTED DISCONNECT.
8) PROVIDE 24" HIGH STANDARD ROOF CURB WITH WOOD NAILER.
9) PROVIDE LOW LEAKAGE MOTORIZED OUTSIDE AIR DAMPERS.
10) UNIT TO BE ETL, UL, OR CSA LABELED.
11) PROVIDE UNIT INTERIOR AND EXTERIOR CASINGS TO BE ELECTRO-STATIC POWDER COATED AND OVEN BAKED PER ASTM B-117, 5000 HOUR RATING. (THERMAL BREAK)
12) CABINET WALLS AND FLOOR INSULATION TO BE 2" FOAM. DOORS TO BE 1" FOAM INSULATION. FIBERGLASS NOT APPROVED.
13) PROVIDE DOUBLE SLOPED STAINLESS STEEL DRAIN PAN.
14) PROVIDE DDC CONTROLLER WITH SELF-CONTAINING SA TEMP AND HUMIDITY SENSORS. DDC CONTROLLER TO HAVE BACNET IP OR LONWORKS INTERFACE.
15) PROVIDE 2" DEFLECTION SPRING ISOLATORS FOR SUPPLY FAN AND RIS ISOLATION FOR COMPRESSORS.
16) PROVIDE FACTORY FULL OPERATIONAL TEST REPORT BEFORE SHIPMENT AND CERTIFIED START-UP.

## VALENT VX-SERIES @ 460-3-60
VALENT VX- SERIES 100% OUTSIDE AIR DX ROOFTOP PACKAGED UNITS @ 460/3/60
NOM TONS | 7.5 | 12.5 | 15 | 17.5 | 20 | 25 | 30
MODEL NUMBER | VX-112-7.5 | VX-112-12.5 | VX-212-15 | VX-12-17.5 | VX-212-20 | VX-212-25 | VX-212-30
AMBIENT TEMP. | 95 | 95 | 95 | 95 | 95 | 95 | 95
REFRIGERANT | R-410A | R-410A | R-410A | R-410A | R-410A | R-410A | R-410A
TOTAL / SENS. (MBH) @ 91.8 / 80.2 | 94.5 / 41.1 | 151.7 / 65.8 | 191.5 / 83.3 | 230.5 / 100.5 | 269.5 / 117.9 | 331.2 / 144.1 | 371.3 / 161.8
LEAVING DB / WB (F) | 54.6 / 54.6 | 52.1 / 52.1 | 54.2 / 54.2 | 55.5 / 55.4 | 56.3 / 56.3 | 54.6 / 54.6 | 55.3 / 55.2
HOT GAS REHEAT (MBH) | 43.4 | 57.4 | 79.2 | 90.4 | 101.1 | 121.4 | 135.7
TOTAL CFM | 1000 | 1500 | 2000 | 2500 | 3000 | 3500 | 4000
ESP (W.G.) | 1.00" | 1.00" | 1.00" | 1.00" | 1.00" | 1.00" | 1.00"
COMPR. QTY. / TYPE | 1 / INVERTER SCROLL | 1 / INVERTER SCROLL | 2 / INVERTER SCROLL | 2 / INVERTER SCROLL | 2 / INVERTER SCROLL | 2 / INVERTER SCROLL | 2 / INVERTER SCROLL
BHP / HP MOTOR | 0.287 / 1.0 | 0.467 / 1.0 | 0.745 / 1.0 | 0.759 / 3.0 | 0.97 / 3.0 | 1.228 / 3.0 | 1.545 / 3.0
MCA | 25.4 | 25.4 | 28.4 | 60.5 | 60.5 | 68 | 72.5
MOCP | 30 | 30 | 40 | 70 | 70 | 100 | 100
DIMENSIONS (H, W, L) (IN.) | 65 X 53 X 99 | 60 X 53 X 99 | 76 X 68 X 109 | 76 X 68 X 109 | 76 X 68 X 109 | 76 X 68 X 109 | 76 X 68 X 109
WEIGHT (LBS.) | 2311 | 2444 | 3338 | 3425 | 3546 | 3638 | 3668
FILTERS / QTY. - SIZE (IN.) 2" PLEATED - MERV 8 | 4 - 20 X 20 X 2 | 4 - 20 X 20 X 2 | 8 - 16 X 25 X 2 | 8 - 16 X 25 X 2 | 8 - 16 X 25 X 2 | 8 - 16 X 25 X 2 | 8 - 16 X 25 X 2
HEATER KW @ 460 V | 15 | 15 | 15 | 35 | 35 | 35 | 35
HEATER AMPS | 18.8 | 18.8 | 18.8 | 43.9 | 43.9 | 43.9 | 43.9
SCHEDULE NOTES:
1) BASIS OF DESIGN IS VALENT PRODUCTS.
2) PROVIDE FACTORY-INSTALLED MODULATING HOT GAS REHEAT.
3) PROVIDE 2" DOUBLE WALL, R-13 INTERNAL INSULATION.
4) PROVIDE ELECTRIC HEATER WITH SCR CONTROLLER AND SINGLE POINT POWER.
5) PROVIDE FACTORY-INSTALLED SUPPLY FAN VFD CONTROLLER, PREMIUM EFFICIENCY MOTOR.
6) PROVIDE FACTORY-INSTALLED ELECTRO-FIN COATED CONDENSER AND EVAPORATOR COILS.
7) PROVIDE FACTORY-INSTALLED UNIT MOUNTED DISCONNECT.
8) PROVIDE 24" HIGH STANDARD ROOF CURB WITH WOOD NAILER.
9) PROVIDE LOW LEAKAGE MOTORIZED OUTSIDE AIR DAMPERS.
10) UNIT TO BE ETL, UL, OR CSA LABELED.
11) PROVIDE UNIT INTERIOR AND EXTERIOR CASINGS TO BE ELECTRO-STATIC POWDER COATED AND OVEN BAKED PER ASTM B-117, 5000 HOUR RATING. (THERMAL BREAK)
12) CABINET WALLS AND FLOOR INSULATION TO BE 2" FOAM. DOORS TO BE 1" FOAM INSULATION. FIBERGLASS NOT APPROVED.
13) PROVIDE DOUBLE SLOPED STAINLESS STEEL DRAIN PAN.
14) PROVIDE DDC CONTROLLER WITH SELF-CONTAINING SA TEMP AND HUMIDITY SENSORS. DDC CONTROLLER TO HAVE BACNET IP OR LONWORKS INTERFACE.
15) PROVIDE 2" DEFLECTION SPRING ISOLATORS FOR SUPPLY FAN AND RIS ISOLATION FOR COMPRESSORS.
16) PROVIDE FACTORY FULL OPERATIONAL TEST REPORT BEFORE SHIPMENT AND CERTIFIED START-UP.