## 14.0 SEER
OXBOX J4AC4 / J4AH4P 14.0 SEER RESIDENTIAL SPLIT SYSTEMS @ 208-230/1/60
NOM TONS | 1.5 | 2 | 2.5 | 3 | 3.5 | 4 | 5
SEER | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14 | 14
CONDENSER MODEL NO. | J4AC418 | J4AC424 | J4AC430 | J4AC436 | J4AC442 | J4AC448 | J4AC460
AIR HANDLER MODEL NO. | J4AH4P18 | J4AH4P24 | J4AH4P30 | J4AH4P36 | J4AH4P42 | J4AH4P48 | J4AH4P60
AMBIENT TEMP. | 95 | 95 | 95 | 95 | 95 | 95 | 95
REFRIGERANT | R-410A | R-410A | R-410A | R-410A | R-410A | R-410A | R-410A
TOTAL / SENS. (MBH) @ 80/67 | 18.0 / 13.0 | 23.6 / 16.9 | 29.0 / 21.0 | 36.0 / 26.0 | 42.0 / 30.7 | 48.0 / 35.0 | 57.0 / 41.0
COMPRESSOR QTY. / TYPE | 1 / SCROLL | 1 / SCROLL | 1 / SCROLL | 1 / SCROLL | 1 / SCROLL | 1 / SCROLL | 1 / SCROLL
COMPRESSOR FLA - LRA | 7.7 - 48.0 | 10.1 - 52 | 10.9 - 63 | 14.7 - 75 | 15.9 - 112.3 | 18.3 - 108 | 21 - 127.9
CONDENSER FAN FLA - HP | 0.7 - 1/8 | 0.7 - 1/8 | 1.0 - 1/6 | 1.0 - 1/6 | 1.7 - 1/3 | 1.7 - 1/3 | 1.7 - 1/3
DIMENSIONS (H,W,D) (IN.) | 25 X 22 X 22 | 25 X 24 X 24 | 25 X 28 X 28 | 25 X 29 X 29 | 33 X 28 X 28 | 30 X 30 X 30-1/4 | 32 X 34 X 34
WEIGHT (LBS.) | 121 | 132 | 148 | 154 | 190 | 190 | 203
MCA | 10.4 | 13.4 | 14.7 | 19.4 | 21.6 | 24.6 | 28
MOCP | 15 | 20 | 25 | 30 | 35 | 40 | 45
AIR HANDLER
TOTAL CFM | 600 | 800 | 1000 | 1200 | 1400 | 1600 | 1925
ESP (IN. WG.) | 0.50" | 0.50" | 0.50" | 0.50" | 0.50" | 0.50" | 0.40"
FAN MOTOR HP-FLA | 1/8 - 1.4 | 1/5 - 1.6 | 1/4 - 2.3 | 1/2 - 4.1 | 1/2 - 2.6 | 1/2 - 3.3 | 3/4 - 4.5
DIMENSIONS (H,W,D) (IN.) | 42 X 18 X 21 | 47 X 20 X 22 | 47 X 20 X 22 | 47 X 20 X 22 | 55 X 22 X 24 | 55 X 22 X 24 | 55 X 22 X 24
FILTER / QTY. - SIZE (L, W, H) | 1 - 16 X 20 X 1 | 1 - 18 X 20 X 1 | 1 - 18 X 20 X 1 | 1 - 18 X 20 X 1 | 1 - 20 X 22 X 1 | 1 - 20 X 22 X 1 | 1 - 20 X 22 X 1
WEIGHT (LBS.) | 104 | 125 | 128 | 128 | 159 | 159 | 159
ELECTRIC HEAT KW @ 240/1/60 | 5 | 5 | 5 | 7.5 | 7.5 | 7.5 | 10
MCA @ 208 / 240 | 24.4 / 27.9 | 24.6 / 28.1 | 25.5 / 29.0 | 37.2 / 42.4 | 37.2 / 42.4 | 38.1 / 43.3 | 50.0 / 57.8
MOCP @ 208 / 240 | 25 / 30 | 25 / 30 | 30 / 35 | 40 / 45 | 40 / 45 | 40 / 45 | 50 / 60
SUCTION (IN. OD)*** | 3/4 | 3/4 | 3/4 | 3/4 | 7/8 | 7/8 | 7/8
LIQUID (IN. OD)*** | 3/8 | 3/8 | 3/8 | 3/8 | 3/8 | 3/8 | 3/8
***CONTACT THE MANUFACTURER FOR REFRIGERANT LINE SIZING FOR APPLICATIONS EXCEEDING 50 FEET.***
SCHEDULE NOTES:
1) BASIS OF DESIGN IS OXBOX, A TRANE BRAND.
2) MULTIPOISE AIR HANDLING UNIT WITH PSC MOTOR.

## 14.0 SEER - FRONT RETURN AHU
OXBOX J4AC4 / JMM4A0A (FRONT RETURN AHU) 14.0 SEER RESIDENTIAL SPLIT SYSTEMS @ 208-230/1/60
NOM TONS | 1.5 | 2 | 2.5 | 3
SEER | 14 | 14 | 14 | 14
CONDENSER MODEL NO. | J4AC418 | J4AC424 | J4AC430 | J4AC436
AIR HANDLER MODEL NO. | JMM4A0A18 | JMM4A0A24 | JMM4A0A30 | JMM4A0A36
AMBIENT TEMP. | 95 | 95 | 95 | 95
REFRIGERANT | R-410A | R-410A | R-410A | R-410A
TOTAL / SENS. (MBH) @ 80/67 | 18.0 / 13.0 | 22.8 / 16.5 | 29.0 / 21.0 | 35.4 / 25.7
COMPRESSOR QTY. / TYPE | 1 / SCROLL | 1 / SCROLL | 1 / SCROLL | 1 / SCROLL
COMPRESSOR FLA - LRA | 7.7 - 48.0 | 10.1 - 52 | 10.9 - 63 | 14.7 - 75
CONDENSER FAN FLA - HP | 0.7 - 1/8 | 0.7 - 1/8 | 1.0 - 1/6 | 1.0 - 1/6
DIMENSIONS (H,W,D) (IN.) | 25 X 22 X 22 | 25 X 24 X 24 | 25 X 28 X 28 | 25 X 25 X 29
WEIGHT (LBS.) | 121 | 132 | 148 | 154
MCA | 10.4 | 13.4 | 14.7 | 19.4
MOCP | 15 | 20 | 25 | 30
AIR HANDLER
TOTAL CFM | 600 | 800 | 1000 | 1200
ESP (IN. WG.) | 0.40" | 0.40" | 0.40" | 0.40"
FAN MOTOR HP-FLA | 1/6 - 0.8 | 1/4 - 1.0 | 1/3 - 1.28 | 1.8 - 1/2
DIMENSIONS (H,W,D) (IN.) | 37 X 21 X 17 | 37 X 21 X 17 | 40 X 22 X 19 | 40 X 22 X19
FILTER / QTY. - SIZE (L, W, H) | 1 - 16 X 20 X 1 | 1 - 16 X 20 X 1 | 1 - 20 X 20 X 1 | 1 - 20 X 20 X 1
WEIGHT (LBS.) | 88 | 88 | 106 | 106
ELECTRIC HEAT KW @ 240/1/60 | 5 | 5 | 5 | 7.5
MCA @ 208 / 240 | 23.6 / 27.1 | 23.5 / 27.3 | 24.2 / 27.7 | 36.2 / 41.4
MOCP @ 208 / 240 | 25 / 30 | 25 / 30 | 25 / 30 | 40 / 45
SUCTION (IN. OD)*** | 3/4 | 3/4 | 3/4 | 3/4
LIQUID (IN. OD)*** | 3/8 | 3/8 | 3/8 | 3/8
***CONTACT THE MANUFACTURER FOR REFRIGERANT LINE SIZING FOR APPLICATIONS EXCEEDING 50 FEET.***
SCHEDULE NOTES:
1) BASIS OF DESIGN IS OXBOX, A TRANE BRAND.
2) FRONT RETURN AIR HANDLING UNIT ONLY WITH PSC MOTOR AND ORIFICE FLOW CONTROL.

## 15.0 SEER
OXBOX J4AC4 / J4AH4E 15.0 SEER RESIDENTIAL SPLIT SYSTEMS @ 208-230/1/60
NOM TONS | 1.5 | 2 | 2.5 | 3 | 3.5 | 4 | 5
SEER | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14 | 14
CONDENSER MODEL NO. | J4AC418 | J4AC424 | J4AC430 | J4AC436 | J4AC442 | J4AC448 | J4AC460
AIR HANDLER MODEL NO. | J4AH4E24 | J4AH4E24 | J4AH4E36 | J4AH4E60 | J4AH4E60 | J4AH4E60 | J4AH4E60
AMBIENT TEMP. | 95 | 95 | 95 | 95 | 95 | 95 | 95
REFRIGERANT | R-410A | R-410A | R-410A | R-410A | R-410A | R-410A | R-410A
TOTAL / SENS. (MBH) @ 80/67 | 18.0 / 13.0 | 23.4 / 16.9 | 29.0 / 21.0 | 36.0 / 26.0 | 42.0 / 30.7 | 48.0 / 35.0 | 57.0 / 41.0
COMPRESSOR QTY. / TYPE | 1 / SCROLL | 1 / SCROLL | 1 / SCROLL | 1 / SCROLL | 1 / SCROLL | 1 / SCROLL | 1 / SCROLL
COMPRESSOR FLA - LRA | 7.7 - 48.0 | 10.1 - 52 | 10.9 - 63 | 14.7 - 75 | 15.9 - 112.3 | 18.3 - 108 | 21 - 127.9
CONDENSER FAN FLA - HP | 0.7 - 1/8 | 0.7 - 1/8 | 1.0 - 1/6 | 1.0 - 1/6 | 1.7 - 1/3 | 1.7 - 1/3 | 1.7 - 1/3
DIMENSIONS (H,W,D) (IN.) | 25 X 22 X 22 | 25 X 24 X 24 | 25 X 28 X 28 | 25 X 29 X 29 | 33 X 28 X 28 | 30 X 30 X 30-1/4 | 32 X 34 X 34
WEIGHT (LBS.) | 121 | 132 | 148 | 154 | 190 | 190 | 203
MCA | 10.4 | 13.4 | 14.7 | 19.4 | 21.6 | 24.6 | 28
MOCP | 15 | 20 | 25 | 30 | 35 | 40 | 45
AIR HANDLER
TOTAL CFM | 600 | 800 | 1000 | 1200 | 1400 | 1600 | 1925
ESP (IN. WG.) | 0.50" | 0.50" | 0.50" | 0.50" | 0.50" | 0.50" | 0.40"
FAN MOTOR HP-FLA | 1/3 - 2.6 | 1/3 - 2.6 | 1/2 - 3.0 | 1/2 - 3.0 | 3/4 - 4.5 | 3/4 - 4.5 | 3/4 - 4.5
DIMENSIONS (H,W,D) (IN.) | 42 X 18 X 21 | 47 X 20 X 22 | 47 X 20 X 22 | 47 X 20 X 22 | 55 X 22 X 24 | 55 X 22 X 24 | 55 X 22 X 24
FILTER / QTY. - SIZE (L, W, H) | 1 - 16 X 20 X 1 | 1 - 16 X 20 X 1 | 1 - 18 X 20 X 1 | 1 - 18 X 20 X 1 | 1 - 20 X 22 X 1 | 1 - 20 X 22 X 1 | 1 - 20 X 22 X 1
WEIGHT (LBS.) | 104 | 125 | 128 | 128 | 159 | 159 | 159
ELECTRIC HEAT KW @ 240/1/60 | 5 | 5 | 5 | 7.5 | 7.5 | 10 | 10
MCA @ 208 / 240 | 25.9 / 29.4 | 25.9 / 29.4 | 26.4 / 29.9 | 37.7 / 42.9 | 39.6 / 44.8 | 50.9 / 57.8 | 50.9 / 57.8
MOCP @ 208 / 240 | 30 / 30 | 30 / 30 | 30 / 30 | 40 / 45 | 40 / 45 | 60 / 60 | 50 / 60
SUCTION (IN. OD)*** | 3/4 | 3/4 | 3/4 | 3/4 | 7/8 | 7/8 | 7/8
LIQUID (IN. OD)*** | 3/8 | 3/8 | 3/8 | 3/8 | 3/8 | 3/8 | 3/8
***CONTACT THE MANUFACTURER FOR REFRIGERANT LINE SIZING FOR APPLICATIONS EXCEEDING 50 FEET.***
SCHEDULE NOTES:
1) BASIS OF DESIGN IS OXBOX, A TRANE BRAND.
2) MULTIPOISE AIR HANDLING UNIT WITH ECM MOTOR.

## 16.0 SEER
OXBOX J4AC6 / J4AH4E 16.0 SEER RESIDENTIAL SPLIT SYSTEMS @ 208-230/1/60
NOM TONS | 1.5 | 2 | 2.5 | 3 | 3.5 | 4
SEER | 16 | 16 | 16 | 16 | 16 | 16
CONDENSER MODEL NO. | J4AC618 | J4AC624 | J4AC630 | J4AC636 | J4AC642 | J4AC648
AIR HANDLER MODEL NO. | J4AH4E24 | J4AH4E24 | JMM5A0B30M | J4AH4E60 | J4AH4E60 | J4AH4E60
AMBIENT TEMP. | 95 | 95 | 95 | 95 | 95 | 95
REFRIGERANT | R-410A | R-410A | R-410A | R-410A | R-410A | R-410A
TOTAL / SENS. (MBH) @ 80/67 | 18.8 / 13.6 | 24.8 / 18.0 | 30.0 / 21.8 | 35.0 / 25.4 | 42.0 / 30.7 | 48.0 / 35.0
COMPRESSOR QTY. / TYPE | 1 / SCROLL | 1 / SCROLL | 1 / SCROLL | 1 / SCROLL | 1 / SCROLL | 1 / SCROLL
COMPRESSOR FLA - LRA | 7.7 - 48.0 | 10.1 - 52 | 12.4 - 63 | 19.4 - 30 | 15.9 - 112.3 | 18.3 - 108
CONDENSER FAN FLA - HP | 0.7 - 1/8 | 1.0 - 1/6 | 1.0 - 1/6 | 1.0 - 1/6 | 1.7 - 1/3 | 1.7 - 1/3
DIMENSIONS (H,W,D) (IN.) | 25 X 24 X 24 | 25 X 28 X 28 | 25 X 29 X 29 | 33 X 29 X 29 | 33 X 28 X 28 | 30 X 30 X 30-1/4
WEIGHT (LBS.) | 128 | 148 | 157 | 176 | 190 | 190
MCA | 10.4 | 13.7 | 16.5 | 19.4 | 21.6 | 24.6
MOCP | 15 | 20 | 25 | 30 | 35 | 40
AIR HANDLER
TOTAL CFM | 600 | 800 | 1000 | 1200 | 1400 | 1600
ESP (IN. WG.) | 0.50" | 0.50" | 0.40" | 0.50" | 0.50" | 0.50"
FAN MOTOR HP-FLA | 1/3 - 2.6 | 1/3 - 2.6 | 1/2 - 2.7 | 1/2 - 3.0 | 3/4 - 4.5 | 3/4 - 4.5
DIMENSIONS (H,W,D) (IN.) | 42 X 18 X 21 | 42 X 18 X 21 | 40 X 22 X 19 | 55 X 22 X 24 | 55 X 22 X 24 | 55 X 22 X 24
FILTER / QTY. - SIZE (L, W, H) | 1 - 16 X 20 X 1 | 1 - 16 X 20 X 1 | 1 - 20 X 20 X 1 | 1 - 20 X 22 X 1 | 1 - 20 X 22 X 1 | 1 - 20 X 22 X 1
WEIGHT (LBS.) | 101 | 101 | 97 | 159 | 159 | 159
ELECTRIC HEAT KW @ 240/1/60 | 5 | 5 | 5 | 7.5 | 7.5 | 10
MCA @ 208 / 240 | 25.9 / 29.4 | 25.9 / 29.4 | 26.0 / 29.5 | 39.6 / 44.8 | 39.6 / 44.8 | 50.9 / 57.8
MOCP @ 208 / 240 | 30 / 30 | 30 / 30 | 30 / 30 | 40 / 45 | 40 / 45 | 60 / 60
SUCTION (IN. OD)*** | 3/4 | 3/4 | 3/4 | 3/4 | 7/8 | 7/8
LIQUID (IN. OD)*** | 3/8 | 3/8 | 3/8 | 3/8 | 3/8 | 3/8
***CONTACT THE MANUFACTURER FOR REFRIGERANT LINE SIZING FOR APPLICATIONS EXCEEDING 50 FEET.***
SCHEDULE NOTES:
1) BASIS OF DESIGN IS OXBOX, A TRANE BRAND.
2) J4AH4E IS MULTIPOISE AIR HANDLING UNIT WTH ECM MOTOR.
3) JMM5A0B IS FRONT RETURN AIR HANDLING UNIT WITH PSC MOTOR AND TX VALVE.

## 14.0 SEER HEAT PUMP PKG. UNIT
OXBOX J4PH4 14.0 SEER HEAT PUMP PACKAGED UNITS @ 208-230/1/60
NOM TONS | 2 | 2.5 | 3 | 3.5 | 4 | 5
SEER | 14 | 14 | 14 | 14 | 14 | 14
MODEL NUMBER | J4PH4024 | J4PH4030 | J4PH4036 | J4PH4042 | J4PH4048 | J4PH4060
AMBIENT TEMP. | 95 | 95 | 95 | 95 | 95 | 95
REFRIGERANT | R-410A | R-410A | R-410A | R-410A | R-410A | R-410A
TOTAL / SENS. (MBH) @ 80/67 | 23.5 / 17.0 | 29.0 / 21.0 | 34.5 / 25.0 | 41.0 / 29.8 | 49.0 / 35.5 | 57.0 / 41.3
TOTAL CFM | 800 | 1000 | 1200 | 1400 | 1600 | 1900
ESP (WG) | 0.50" | 0.50" | 0.50" | 0.50" | 0.50" | 0.50"
COMPR. QTY. / TYPE | 1 - ROTARY | 1 - ROTARY | 1 - ROTARY | 1 - SCROLL | 1 - SCROLL | 1 / SCROLL
COMPR. FLA - LRA | 8.45 - 34.8 | 12.0 - 59.9 | 13.0 - 75 | 15.2 - 112.3 | 17.3 - 108 | 21.5 - 125
COND FAN / FLA - HP | 0.68 - 1/12 | 1.0 - 1/6 | 1.0 - 1/6 | 1.67 - 1/3 | 1.67 - 1/3 | 1.67 - 1/3
EVAP FAN / FLA - HP | 2.46 - 1/4 | 4.1 - 1/2 | 4.1 - 1/2 | 2.8 - 3/4 | 3.6 - 3/4 | 6.0 - 3/4
MCA | 13.7 | 20.1 | 21.4 | 23.5 | 26.9 | 34.6
MOCP | 20 | 30 | 30 | 30 | 40 | 50
DIMENSIONS (H,W,D) (IN.) | 25 X 52 X 38 | 25 X 52 X 38 | 25 X 52 X 38 | 33 X 59 X 42 | 33 X 59 X 42 | 33 X 59 X 42
WEIGHT (LBS.) | 326 | 346 | 351 | 463 | 463 | 479
FILTERS | 1" | 1" | 1" | 1" | 1" | 1"
HEATER KW | 5 | 5 | 7.5 | 7.5 | 7.5 | 10
MCA @ 208 / 240 | 27.9 / 31.4 | 23.0 / 26.0 | 34.0 / 39.0 | 34.0 / 39.0 | 34.0 / 39.0 | 45.0 / 52.0
MOCP @ 208 / 240 | 30 / 35 | 25 / 30 | 35 / 40 | 35 / 40 | 35 / 40 | 45 / 60
SCHEDULE NOTES:
1) BASIS OF DESIGN IS OXBOX, A TRANE BRAND.