## 85-95 208-1-60
|  | Supply Fan |  | Heat Pump Cooling | [8 empty] | Heat Pump Heating | [5 empty] | Unit Electrical
Tag | Model | CFM | ESP | Net Total Capacity | Net Sensible Capacity | EAT DB/WB | LAT DB/WB | Fluid Flow | EWT | LWT | WPD | EER* | Total Capacity | EAT DB | LAT DB | EWT | LWT | COP* | FLA | MCA | MOCP | Unit Voltage
HP-1.25T | 50WDE015 | 500 | 0.5 | 14 | 11.6 | 75/63 | 53.5/53.2 | 3.5 | 85 | 95 | 8.2 | 15.5 | 19.8 | 68 | 104.6 | 70 | 60.8 | 5.2 | 10.2 | 11.7 | 15 | 208/230-1-60
HP-1.5T | 50WDE018 | 600 | 0.5 | 18.5 | 14.7 | 75/63 | 52.3/52.1 | 4.2 | 85 | 95 | 6.3 | 15.5 | 22.9 | 68 | 103.3 | 70 | 61.2 | 5 | 11.8 | 13.7 | 20 | 208/230-1-60
HP-2.0T | 50WDE024 | 800 | 0.5 | 23.7 | 18.8 | 75/63 | 53.2/52.6 | 5.6 | 85 | 95 | 7.5 | 15.5 | 32.9 | 68 | 106.1 | 70 | 60.6 | 5 | 14.7 | 17.2 | 25 | 208/230-1-60
HP-2.5T | 50WDE030 | 1000 | 0.5 | 30.6 | 25.3 | 75/63 | 53.6/53.2 | 7 | 85 | 95 | 11 | 15 | 38.8 | 68 | 100.8 | 70 | 61.1 | 6.3 | 19.6 | 23.2 | 35 | 208/230-1-60
HP-3.0T | 50WDE036 | 1200 | 0.5 | 36 | 28.7 | 75/63 | 52.9/52.4 | 8.4 | 85 | 95 | 14.7 | 15 | 45.5 | 68 | 103.1 | 70 | 61.4 | 6.1 | 23 | 26.6 | 40 | 208/230-1-60
HP-3.5T | 50WDE042 | 1500 | 0.5 | 42 | 32.1 | 75/63 | 54.7/53.9 | 9.8 | 85 | 95 | 13.6 | 15 | 54.5 | 68 | 99.3 | 70 | 61.2 | 5 | 26.6 | 31.2 | 45 | 208/230-1-60
HP-4.0T | 50WDE048 | 1600 | 0.5 | 45 | 37 | 75/63 | 53.6/53.1 | 11.2 | 85 | 95 | 8.1 | 15 | 63 | 68 | 104.5 | 70 | 61.1 | 5.9 | 26.7 | 31.3 | 45 | 208/230-1-60
HP-5.0T | 50WDE060 | 2000 | 0.5 | 59.1 | 47.2 | 75/63 | 53.2/52.6 | 14 | 85 | 95 | 12.3 | 14.5 | 70.4 | 68 | 100.6 | 70 | 62.1 | 6.3 | 34.3 | 40.6 | 60 | 208/230-1-60
HP-6.0T | 50WDE070 | 2415 | 0.5 | 60.3 | 52.4 | 75/63 | 54.9/54.3 | 16.8 | 85 | 95 | 17.1 | 14 | 81.8 | 68 | 102.5 | 70 | 62.2 | 5.1 | 37.1 | 44.1 | 70 | 208/230-1-60
* EER & COP AT AHRI
1. Carrier is the basis of design; Bosch and Climate Master are acceptable, subject to complete compliance with schedule and notes.
2. Non-combustile stand for all vertical units.
3. Horizontal units must include rubber isolators for hanging.
4. Provide programmable thermostat for all units.
5. Mfg. to verify all listed capacities.
6. Plenum rated stainless steel over braid hose with full port ball valves (return valve w/ memory stop).
7. Hand of units to be coordinated.
8. Quiet sound package shall include as a minimum: compressor blankets and rubber isolators under compressors.
9. Microprocessor control circuit module for: anti-short cycle protection, high and low pressure cutouts, water coil freeze protection, condensate overflow protection, random start, remote fault monitoring, over/under voltage protection, diagnostic LED, reset lockout at unit. or disconnect. Condensate overflow protection shall be factory installed and wired.
10. ECM motor for all units.
11. Condensers shall be copper coaxial type.
12. All units are ARI/ISO and UL/ETL listed as factory assembled package.
13. Stainless steel drain pan, including condensate overflow safety switch.
14. All units shall comply with ASHRAE 90.1.
15. Manufacturer to provide vertical units with internal condensate drain p-traps or mechanical contractor shall install external p-traps in the field. Mechanical contractor to install condensate p-traps on all horizontal units.
16. Hot gas reheat shall be provided for all units 4.0T and above. Shall be controlled with humidistat and start unit in reheat mode when humidity is above set point once space temp is satisfied.
17. Hot gas bypass to be provided with factory installed controls to prevent air coils from frost development. All units 4.0T and above.
18. A2L refrigerant leak detection to be included.
19. Units shall have a 2-way electronic solenoid valve mounted internally in the unit cabinet. Valve shall be factory wired to open with compressor operation.
20. [optional] Provide low speed dehumidification option for all units. Units must have the ability to modulate fan speed when a call for dehumidification is made.
21. Finned tube heat exchanger to be constructed of aluminum fins not exceeding 16 fins per inch, bonded to rifled copper tubes.
22. Flow proving switch (differential pressure switch) to shut down unit on loss of flow without going to hard reset.
23. Two-stage unit for 2.0T and above.

## 85-95 277-1-60
|  | Supply Fan |  | Heat Pump Cooling | [8 empty] | Heat Pump Heating | [5 empty] | Unit Electrical
Tag | Model | CFM | ESP | Net Total Capacity | Net Sensible Capacity | EAT DB/WB | LAT DB/WB | Fluid Flow | EWT | LWT | WPD | EER* | Total Capacity | EAT DB | LAT DB | EWT | LWT | COP* | FLA | MCA | MOCP | Unit Voltage
HP-1.25T | 50WDE015 | 500 | 0.5 | 14 | 11.6 | 75/63 | 53.5/53.2 | 3.5 | 85 | 95 | 8.2 | 15.5 | 19.8 | 68 | 104.6 | 70 | 60.8 | 5.2 | 9.4 | 10.6 | 15 | 265-1-60
HP-1.5T | 50WDE018 | 600 | 0.5 | 18.5 | 14.7 | 75/63 | 52.3/52.1 | 4.2 | 85 | 95 | 6.3 | 15.5 | 22.9 | 68 | 103.3 | 70 | 61.2 | 5 | 12.3 | 14.2 | 20 | 265-1-60
HP-2.0T | 50WDE024 | 800 | 0.5 | 23.7 | 18.8 | 75/63 | 53.2/52.6 | 5.6 | 85 | 95 | 7.5 | 15.5 | 32.9 | 68 | 106.1 | 70 | 60.6 | 5 | 12.5 | 14.5 | 20 | 265-1-60
HP-2.5T | 50WDE030 | 1000 | 0.5 | 30.6 | 25.3 | 75/63 | 53.6/53.2 | 7 | 85 | 95 | 11 | 15 | 38.8 | 68 | 100.8 | 70 | 61.1 | 6.3 | 13.3 | 15.4 | 20 | 265-1-60
HP-3.0T | 50WDE036 | 1200 | 0.5 | 36 | 28.7 | 75/63 | 52.9/52.4 | 8.4 | 85 | 95 | 14.7 | 15 | 45.5 | 68 | 103.1 | 70 | 61.4 | 6.1 | 20.1 | 23.2 | 35 | 265-1-60
* EER & COP AT AHRI
1. Carrier is the basis of design; Bosch and Climate Master are acceptable, subject to complete compliance with schedule and notes.
2. Non-combustile stand for all vertical units.
3. Horizontal units must include rubber isolators for hanging.
4. Provide programmable thermostat for all units.
5. Mfg. to verify all listed capacities.
6. Plenum rated stainless steel over braid hose with full port ball valves (return valve w/ memory stop).
7. Hand of units to be coordinated.
8. Quiet sound package shall include as a minimum: compressor blankets and rubber isolators under compressors.
9. Microprocessor control circuit module for: anti-short cycle protection, high and low pressure cutouts, water coil freeze protection, condensate overflow protection, random start, remote fault monitoring, over/under voltage protection, diagnostic LED, reset lockout at unit. or disconnect. Condensate overflow protection shall be factory installed and wired.
10. ECM motor for all units.
11. Condensers shall be copper coaxial type.
12. All units are ARI/ISO and UL/ETL listed as factory assembled package.
13. Stainless steel drain pan, including condensate overflow safety switch.
14. All units shall comply with ASHRAE 90.1.
15. Manufacturer to provide vertical units with internal condensate drain p-traps or mechanical contractor shall install external p-traps in the field. Mechanical contractor to install condensate p-traps on all horizontal units.
16. Hot gas reheat shall be provided for all units 4.0T and above. Shall be controlled with humidistat and start unit in reheat mode when humidity is above set point once space temp is satisfied.
17. Hot gas bypass to be provided with factory installed controls to prevent air coils from frost development. All units 4.0T and above.
18. A2L refrigerant leak detection to be included.
19. Units shall have a 2-way electronic solenoid valve mounted internally in the unit cabinet. Valve shall be factory wired to open with compressor operation.
20. [optional] Provide low speed dehumidification option for all units. Units must have the ability to modulate fan speed when a call for dehumidification is made.
21. Finned tube heat exchanger to be constructed of aluminum fins not exceeding 16 fins per inch, bonded to rifled copper tubes.
22. Flow proving switch (differential pressure switch) to shut down unit on loss of flow without going to hard reset.
23. Two-stage unit for 2.0T and above.

## 85-95 208-3-60
|  | Supply Fan |  | Heat Pump Cooling | [8 empty] | Heat Pump Heating | [5 empty] | Unit Electrical
Tag | Model | CFM | ESP | Net Total Capacity | Net Sensible Capacity | EAT DB/WB | LAT DB/WB | Fluid Flow | EWT | LWT | WPD | EER* | Total Capacity | EAT DB | LAT DB | EWT | LWT | COP* | FLA | MCA | MOCP | Unit Voltage
HP-2.0T | 50WDE024 | 800 | 0.5 | 23.7 | 18.8 | 75/63 | 53.2/52.6 | 5.6 | 85 | 95 | 7.5 | 15.5 | 32.9 | 68 | 106.1 | 70 | 60.6 | 5 | 10.7 | 12.3 | 15 | 208/230-3-60
HP-2.5T | 50WDE030 | 1000 | 0.5 | 30.6 | 25.3 | 75/63 | 53.6/53.2 | 7 | 85 | 95 | 11 | 15 | 38.8 | 68 | 100.8 | 70 | 61.1 | 6.3 | 12.9 | 14.9 | 20 | 208/230-3-60
HP-3.0T | 50WDE036 | 1200 | 0.5 | 36 | 28.7 | 75/63 | 52.9/52.4 | 8.4 | 85 | 95 | 14.7 | 15 | 45.5 | 68 | 103.1 | 70 | 61.4 | 6.1 | 18.3 | 20.7 | 30 | 208/230-3-60
HP-3.5T | 50WDE042 | 1500 | 0.5 | 42 | 32.1 | 75/63 | 54.7/53.9 | 9.8 | 85 | 95 | 13.6 | 15 | 54.5 | 68 | 99.3 | 70 | 61.2 | 5 | 19.9 | 22.7 | 30 | 208/230-3-60
HP-4.0T | 50WDE048 | 1600 | 0.5 | 45 | 37 | 75/63 | 53.6/53.1 | 11.2 | 85 | 95 | 8.1 | 15 | 63 | 68 | 104.5 | 70 | 61.1 | 5.9 | 20.3 | 23.3 | 35 | 208/230-3-60
HP-5.0T | 50WDE060 | 2000 | 0.5 | 59.1 | 47.2 | 75/63 | 53.2/52.6 | 14 | 85 | 95 | 12.3 | 14.5 | 70.4 | 68 | 100.6 | 70 | 62.1 | 6.3 | 22.9 | 26.3 | 40 | 208/230-3-60
HP-6.0T | 50WDE070 | 2415 | 0.5 | 60.3 | 52.4 | 75/63 | 54.9/54.3 | 16.8 | 85 | 95 | 17.1 | 14 | 81.8 | 68 | 102.5 | 70 | 62.2 | 5.1 | 28 | 32.7 | 50 | 208/230-3-60
* EER & COP AT AHRI
1. Carrier is the basis of design; Bosch and Climate Master are acceptable, subject to complete compliance with schedule and notes.
2. Non-combustile stand for all vertical units.
3. Horizontal units must include rubber isolators for hanging.
4. Provide programmable thermostat for all units.
5. Mfg. to verify all listed capacities.
6. Plenum rated stainless steel over braid hose with full port ball valves (return valve w/ memory stop).
7. Hand of units to be coordinated.
8. Quiet sound package shall include as a minimum: compressor blankets and rubber isolators under compressors.
9. Microprocessor control circuit module for: anti-short cycle protection, high and low pressure cutouts, water coil freeze protection, condensate overflow protection, random start, remote fault monitoring, over/under voltage protection, diagnostic LED, reset lockout at unit. or disconnect. Condensate overflow protection shall be factory installed and wired.
10. ECM motor for all units.
11. Condensers shall be copper coaxial type.
12. All units are ARI/ISO and UL/ETL listed as factory assembled package.
13. Stainless steel drain pan, including condensate overflow safety switch.
14. All units shall comply with ASHRAE 90.1.
15. Manufacturer to provide vertical units with internal condensate drain p-traps or mechanical contractor shall install external p-traps in the field. Mechanical contractor to install condensate p-traps on all horizontal units.
16. Hot gas reheat shall be provided for all units 4.0T and above. Shall be controlled with humidistat and start unit in reheat mode when humidity is above set point once space temp is satisfied.
17. Hot gas bypass to be provided with factory installed controls to prevent air coils from frost development. All units 4.0T and above.
18. A2L refrigerant leak detection to be included.
19. Units shall have a 2-way electronic solenoid valve mounted internally in the unit cabinet. Valve shall be factory wired to open with compressor operation.
20. [optional] Provide low speed dehumidification option for all units. Units must have the ability to modulate fan speed when a call for dehumidification is made.
21. Finned tube heat exchanger to be constructed of aluminum fins not exceeding 16 fins per inch, bonded to rifled copper tubes.
22. Flow proving switch (differential pressure switch) to shut down unit on loss of flow without going to hard reset.
23. Two-stage unit for 2.0T and above.

## 85-95 408-3-60
|  | Supply Fan |  | Heat Pump Cooling | [8 empty] | Heat Pump Heating | [5 empty] | Unit Electrical
Tag | Model | CFM | ESP | Net Total Capacity | Net Sensible Capacity | EAT DB/WB | LAT DB/WB | Fluid Flow | EWT | LWT | WPD | EER* | Total Capacity | EAT DB | LAT DB | EWT | LWT | COP* | FLA | MCA | MOCP | Unit Voltage
HP-2.0T | 50WDE024 | 800 | 0.5 | 23.7 | 18.8 | 75/63 | 53.2/52.6 | 5.6 | 85 | 95 | 7.5 | 15.5 | 32.9 | 68 | 106.1 | 70 | 60.6 | 5 | 8.5 | 9.7 | 15 | 460-3-60
HP-2.5T | 50WDE030 | 1000 | 0.5 | 30.6 | 25.3 | 75/63 | 53.6/53.2 | 7 | 85 | 95 | 11 | 15 | 38.8 | 68 | 100.8 | 70 | 61.1 | 6.3 | 9.8 | 11.1 | 15 | 460-3-60
HP-3.0T | 50WDE036 | 1200 | 0.5 | 36 | 28.7 | 75/63 | 52.9/52.4 | 8.4 | 85 | 95 | 14.7 | 15 | 45.5 | 68 | 103.1 | 70 | 61.4 | 6.1 | 12.3 | 14.2 | 20 | 460-3-60
HP-3.5T | 50WDE042 | 1500 | 0.5 | 42 | 32.1 | 75/63 | 54.7/53.9 | 9.8 | 85 | 95 | 13.6 | 15 | 54.5 | 68 | 99.3 | 70 | 61.2 | 5 | 14 | 15.8 | 20 | 460-3-60
HP-4.0T | 50WDE048 | 1600 | 0.5 | 45 | 37 | 75/63 | 53.6/53.1 | 11.2 | 85 | 95 | 8.1 | 15 | 63 | 68 | 104.5 | 70 | 61.1 | 5.9 | 14.3 | 16.2 | 20 | 460-3-60
HP-5.0T | 50WDE060 | 2000 | 0.5 | 59.1 | 47.2 | 75/63 | 53.2/52.6 | 14 | 85 | 95 | 12.3 | 14.5 | 70.4 | 68 | 100.6 | 70 | 62.1 | 6.3 | 16 | 18.2 | 25 | 460-3-60
HP-6.0T | 50WDE070 | 2415 | 0.5 | 60.3 | 52.4 | 75/63 | 54.9/54.3 | 16.8 | 85 | 95 | 17.1 | 14 | 81.8 | 68 | 102.5 | 70 | 62.2 | 5.1 | 18.2 | 20.5 | 25 | 460-3-60
* EER & COP AT AHRI
1. Carrier is the basis of design; Bosch and Climate Master are acceptable, subject to complete compliance with schedule and notes.
2. Non-combustile stand for all vertical units.
3. Horizontal units must include rubber isolators for hanging.
4. Provide programmable thermostat for all units.
5. Mfg. to verify all listed capacities.
6. Plenum rated stainless steel over braid hose with full port ball valves (return valve w/ memory stop).
7. Hand of units to be coordinated.
8. Quiet sound package shall include as a minimum: compressor blankets and rubber isolators under compressors.
9. Microprocessor control circuit module for: anti-short cycle protection, high and low pressure cutouts, water coil freeze protection, condensate overflow protection, random start, remote fault monitoring, over/under voltage protection, diagnostic LED, reset lockout at unit. or disconnect. Condensate overflow protection shall be factory installed and wired.
10. ECM motor for all units.
11. Condensers shall be copper coaxial type.
12. All units are ARI/ISO and UL/ETL listed as factory assembled package.
13. Stainless steel drain pan, including condensate overflow safety switch.
14. All units shall comply with ASHRAE 90.1.
15. Manufacturer to provide vertical units with internal condensate drain p-traps or mechanical contractor shall install external p-traps in the field. Mechanical contractor to install condensate p-traps on all horizontal units.
16. Hot gas reheat shall be provided for all units 4.0T and above. Shall be controlled with humidistat and start unit in reheat mode when humidity is above set point once space temp is satisfied.
17. Hot gas bypass to be provided with factory installed controls to prevent air coils from frost development. All units 4.0T and above.
18. A2L refrigerant leak detection to be included.
19. Units shall have a 2-way electronic solenoid valve mounted internally in the unit cabinet. Valve shall be factory wired to open with compressor operation.
20. [optional] Provide low speed dehumidification option for all units. Units must have the ability to modulate fan speed when a call for dehumidification is made.
21. Finned tube heat exchanger to be constructed of aluminum fins not exceeding 16 fins per inch, bonded to rifled copper tubes.
22. Flow proving switch (differential pressure switch) to shut down unit on loss of flow without going to hard reset.
23. Two-stage unit for 2.0T and above.